BIMGUARD AI

Automated BIM Corrosion Compliance Checker

Final Master Project

Masters in BIM Management

Zigurat Global Institute of Technology

Group 5

Methodology: OpenBIM  |  IFC (ISO 16739-1)  |  BCF 2.1  |  ISO 19650

Corrosion Engines: GC-001 (Galvanic)  |  CC-001 (Crevice)

Platform: Python  |  Streamlit  |  ifcopenshell

# Abstract

Corrosion in Mechanical, Electrical and Plumbing (MEP) building services is a significant and under-addressed risk. It, and the spatial conflict that seismic restraint creates, are detected late, when remediation is most expensive: existing BIM coordination tools check geometry rather than material chemistry, and reserve no space for the bracing MEP distribution later requires.

This thesis presents BIMGUARD AI, an OpenBIM compliance checker that reads Industry Foundation Classes (IFC) files and applies five corrosion engines and one spatial engine. GC-001 checks galvanic corrosion against NASA-STD-6012 voltage thresholds and CC-001 crevice corrosion using EN ISO 15329:2007 wetting classes. MC-001 scores microbially influenced corrosion, MM-001 material-media compatibility across twelve materials and eight media, and XM-001 the galvanic couple formed where dissimilar modelled elements meet. Blue Halo reserves seismic bracing clearance at LOD 300, reporting spatial conflicts while services can still be moved.

Validation on a 25-element synthetic dataset returned 9 Critical, 7 High and 9 Medium issues, an estimated £170,600 cost impact and 162 working days of programme delay. An SS316 flange in a pool plant room scored 0.00 on galvanic risk but 0.89 on crevice risk, showing that single-mechanism checking is insufficient. A formal Expert Review process defines the roles, rubric and feedback cycle governing extracted rules and engine findings, and declares which parts of it are not yet built.

Output is BCF 2.1 throughout. Every threshold traces to a named standard under a White Box architecture, and values no standard fixes are tagged provisional rather than asserted, leaving the tool auditable and vendor-neutral.

Keywords: BIM compliance checking, corrosion risk, galvanic corrosion, crevice corrosion, microbially influenced corrosion, material-media compatibility, seismic bracing clearance, expert review, IFC, OpenBIM, BCF 2.1, MEP coordination, automated rule checking, ISO 19650

# Table of Contents

Abstract	2

Table of Contents	3

List of Tables	6

List of Figures	6

List of Abbreviations	6

Chapter 1 — Introduction	8

1.1  Background and context	8

1.2  Research questions	8

1.3  Project scope	8

1.4  Methodology overview	9

Chapter 2 — Literature Review: Galvanic Corrosion	10

2.1  Electrochemical theory of galvanic corrosion	10

2.2  Galvanic corrosion in MEP building services	10

2.3  Existing AI and computational approaches to corrosion prediction	11

2.4  BIM automation for compliance checking	11

2.5  Identified research gap	12

Chapter 3 — Methodology: GC-001 Galvanic Corrosion Engine	13

3.1  Ruleset development process	13

3.2  Galvanic series and material potential table	13

3.3  Environment classification	13

3.4  Area ratio risk bands	14

3.5  PREN adequacy check	14

3.6  Weighted composite scoring model	14

3.7  Validation approach	15

Chapter 4 — System Architecture	16

4.1  White Box Architecture rationale	16

4.2  IFC parser module	16

4.3  Compliance runner	17

4.4  BCF 2.1 output structure	17

4.5  Streamlit web application	17

4.6  Blue Halo algorithm: seismic bracing clearance reservation	19

4.6.1  Motivation and problem statement	19

4.6.2  Algorithm architecture	19

4.6.3  Brace families and clearance calculation	19

4.6.4  Jurisdiction configuration and value provenance	20

4.6.5  Spatial conflict detection and resolution	21

4.6.6  Worked example: hospital MEP zone	22

4.6.7  Standards cited and data limitations	22

4.6.8  Innovation and contribution	23

Chapter 5 — Results and Discussion: GC-001	23

5.1  Validation dataset results	23

5.2  Cost and programme impact	24

5.3  Limitations	24

5.4  Innovation contribution	24

Chapter 6 — Conclusions: Part I	25

Chapter 7 — Crevice Corrosion Module: Rationale and Research Gap	26

7.1  Limitations of galvanic-only checking	26

7.2  The pool plant room finding	26

Chapter 8 — Literature Review: Crevice Corrosion	27

8.1  Mechanism and four-stage process	27

8.2  Critical Crevice Corrosion Temperature	27

8.3  Relevant standards and test methods	28

Chapter 9 — Methodology: CC-001 Crevice Corrosion Engine	29

9.1  CCT table and stainless steel grades	29

9.2  Geometry classification	29

9.3  Joint type library	29

9.4  Environment severity classification	30

9.5  Weighted composite scoring model	30

9.6  Combined risk assessment function	30

Chapter 10 — Architecture: Combined Compliance System	31

10.1  Pset_CreviceCorrosionRisk schema	31

10.2  Combined asset register	31

10.3  Dual-engine BCF output	31

Chapter 11 — Discussion and Further Development	33

11.1  MIC as the third corrosion module	33

11.2  BMS integration	33

11.3  Weld quality extension	33

11.4  Regulatory context and wider applicability	34

Chapter 12 — Microbially Influenced Corrosion Module (MC-001)	35

12.1  Introduction and rationale	35

12.2  The three MIC organism groups in building services	35

12.2.1  Sulphate-reducing bacteria (SRB)	35

12.2.2  Iron-oxidising bacteria (IOB)	36

12.2.3  Acid-producing bacteria (APB)	36

12.3  MC-001 methodology — scoring model	36

12.3.1  Flow velocity risk (weight: 0.35)	37

12.3.2  Temperature risk (weight: 0.30)	37

12.3.3  Dead-leg risk (weight: 0.25)	37

12.3.4  Material susceptibility (weight: 0.10)	38

12.4  System type modifiers	38

12.5  Under-insulation corrosion pathway	38

12.6  MC-001 risk bands and BCF output	39

12.7  Validation results	39

12.8  Integration with GC-001, CC-001, and the combined compliance framework	40

12.9  Regulatory context and further development	40

12.10  Key finding — fire suppression systems	41

Chapter 13 — Extended Material Engines: MM-001 and XM-001	42

13.1  Rationale — what the first three engines do not cover	42

13.2  MM-001 — material-media compatibility	42

13.3  XM-001 — cross-material contamination	43

13.4  Integration — two comparator paths	44

13.5  Validation	44

13.6  Approval record and carried limitations	45

Chapter 14 — The Expert Review Process	46

14.1  Why the process exists	46

14.2  Roles and independence	46

14.3  States and the enforcement gate	46

14.4  The review rubric	46

14.5  Failure classes and the feedback cycle	47

14.6  Implementation status	48

References	48

# List of Tables

Table 3.2   Environment class definitions and voltage thresholds (GC-001 v1.0.0)

Table 3.4   GC-001 composite risk score bands

Table 4.6.1   Brace family comparison and default Halo footprints (Blue Halo v0.1, ASCE 7-22 / SMACNA baseline configuration)

Table 4.6.2   Configuration parameter comparison across jurisdictions, with the provenance tag Blue Halo assigns to each value

Table 4.6.3   Algorithm output for the hospital corridor, by brace family

Table 5.1   GC-001 validation dataset results by risk band

Table 9.1   CCT values for selected grades (ASTM G48 Method B / CIRIA C692)

Table 9.2   Geometry class definitions and risk multipliers (CC-001 v1.0.0)

Table 12.1   MC-001 flow velocity risk classes (source: CIBSE TM13:2013 / HSE HSG274 Part 2)

Table 12.2   MC-001 dead-leg classification by L/D ratio (source: HSE HSG274 Part 2)

Table 12.3   MC-001 risk bands (note lower thresholds than GC-001/CC-001 reflecting public health dimension)

Table 12.4   MC-001 validation results — 10 scenarios, all results consistent with engineering expectation

Table 13.1   MM-001 composite scoring terms, weights and band thresholds

Table 13.2   MM-001 environment severity ladder and its mapping to CC-001 wetting classes

Table 13.3   XM-001 composite scoring terms, separation and mitigation factors

Table 13.4   Test coverage for MM-001 and XM-001 by group

Table 14.1   The five-dimension review rubric for a candidate rule

Table 14.2   Failure classes and the owner each routes to

Table 14.3   Implementation status of the expert review process

# List of Figures

Figure 4.6.1   Halo clearance volume geometry in section for the three brace families, showing the 45° nominal brace vector, the swept reservation prism, and the anchor edge-distance reservation at the structural interface

# List of Abbreviations

| ACI | American Concrete Institute |
| --- | --- |
| AHJ | Authority Having Jurisdiction |
| APB | Acid-Producing Bacteria |
| ASCE | American Society of Civil Engineers |
| BCF | BIM Collaboration Format (buildingSMART) |
| BIM | Building Information Modelling |
| BMS | Building Management System |
| CC-001 | BIMGUARD Crevice Corrosion Ruleset v1.0.0 |
| CCT | Critical Crevice Corrosion Temperature |
| CDE | Common Data Environment |
| EoR | Engineer of Record |
| FMP | Final Master Project |
| GC-001 | BIMGUARD Galvanic Corrosion Ruleset v1.0.0 |
| IDS | Information Delivery Specification |
| IFC | Industry Foundation Classes (ISO 16739-1) |
| IOB | Iron-Oxidising Bacteria |
| LOD | Level of Development (BIMForum LOD Specification) |
| LOIN | Level of Information Need |
| MC-001 | BIMGUARD Microbially Influenced Corrosion Ruleset v1.0.0 |
| MEP | Mechanical, Electrical, and Plumbing |
| MIC | Microbially Influenced Corrosion |
| MM-001 | BIMGUARD Material-Media Compatibility Ruleset v1.0 |
| NFPA | National Fire Protection Association |
| OD | Outside Diameter |
| PREN | Pitting Resistance Equivalent Number |
| Pset | Property Set (IFC schema) |
| SMACNA | Sheet Metal and Air Conditioning Contractors' National Association |
| SRB | Sulphate-Reducing Bacteria |
| XM-001 | BIMGUARD Cross-Material Contamination Ruleset v1.0 |
| ZOI | Zone of Influence (seismic brace tributary length) |

# Chapter 1 — Introduction

## 1.1  Background and context

Corrosion is responsible for an estimated 3.4% of global GDP in direct costs annually (NACE International, 2016). Within the built environment, MEP building services represent a disproportionate share of that burden: pipework, fittings, and support assemblies in plant rooms, risers, and ceiling voids are routinely exposed to humid, chemically active, or chloride-bearing environments that accelerate metallic degradation. Two mechanisms are of particular significance in this context: galvanic corrosion, which arises when dissimilar metals are placed in electrical contact in the presence of an electrolyte; and crevice corrosion, which develops at confined joint geometries where restricted electrolyte circulation produces an aggressive local chemistry capable of destroying the passive oxide films that protect stainless steel grades.

Current BIM coordination practice addresses geometric conflicts between building services — pipe-on-pipe clashes, services penetrating structural elements, and spatial constraints around access routes — but provides no systematic mechanism for detecting material compatibility risks. Corrosion risk assessment, where it occurs at all, depends on the individual experience of the design engineer and produces no machine-readable compliance record. This gap has three practical consequences: corrosion failures that were predictable at the design stage are discovered during construction or operation, when remediation costs are typically six to ten times higher than the equivalent design-stage intervention; regulatory requirements for traceable compliance records under frameworks such as the Building Safety Act 2022 are not satisfied; and the value of BIM investment in the detailed design stage is not fully realised.

## 1.2  Research questions

This project addresses three primary research questions:

- Can corrosion risk in MEP building services be reliably detected from data already present in standard IFC models, without requiring additional manual input or proprietary BIM authoring tool access?

- Can two mechanistically distinct corrosion failure modes — galvanic corrosion and crevice corrosion — be checked simultaneously within a single automated compliance workflow, and does the combined assessment detect risks that either mechanism alone would miss?

- Can an OpenBIM compliance checking tool — one that operates exclusively on open standards and without proprietary APIs — be deployed effectively across the range of authoring environments used by different disciplines on a typical complex project?

## 1.3  Project scope

BIMGUARD AI is scoped to MEP building services in commercial, industrial, and institutional buildings. The tool processes IFC files conforming to IFC 2x3 or IFC4, exported from any compliant authoring tool. It checks all IfcPipeSegment, IfcPipeFitting, IfcValve, and IfcFlowController elements for which material and spatial data is available in the model. Point cloud data in .las, .laz, or .e57 format is accepted as a supplementary input for as-built deviation analysis but is not required for the compliance engines to function.

The two corrosion mechanisms within scope are galvanic corrosion (engine GC-001) and crevice corrosion (engine CC-001). Microbially Influenced Corrosion (MIC) and stress corrosion cracking are identified as future development modules and are outside the current scope. Fire compartmentation checking was identified as a parallel compliance domain but is likewise outside the current scope.

## 1.4  Methodology overview

BIMGUARD AI is built on a White Box Architecture in which every compliance decision is traceable to a named standard and a specific numerical threshold. Artificial intelligence and large language models are used only as a natural language interface layer; all risk scoring is performed by deterministic rule-based engines whose parameters are published in version-controlled JSON rulesets. This architectural decision is deliberate: in a safety-critical compliance context, an auditor must be able to trace any flagged risk to its evidential basis, which a black-box machine learning model cannot provide.

The technical stack is Python and Streamlit, with ifcopenshell as the IFC parsing library. IFC is used because it is the ISO-standardised vendor-neutral exchange format for BIM data; BCF 2.1 is used as the issue output format because it is the buildingSMART open standard for issue tracking, compatible with all OpenBIM platforms. This OpenBIM methodology is a deliberate and academically significant architectural choice — it ensures that BIMGUARD AI can be used on any project regardless of which authoring tools the individual disciplines employ.

# Chapter 2 — Literature Review: Galvanic Corrosion

## 2.1  Electrochemical theory of galvanic corrosion

Galvanic corrosion arises from the electrochemical potential difference between two metallic materials in electrical contact within an electrolyte. The mechanism was first described systematically by Luigi Galvani and Alessandro Volta in the late eighteenth century and has since been formalised through the development of the electrochemical series and the mixed potential theory of Evans (1960). When two metals of differing nobility are connected in an electrolyte, the less noble metal — the anode — undergoes preferential oxidation, releasing metal ions into solution while electrons travel through the metallic conduction path to the more noble metal — the cathode — where reduction reactions occur. The rate of this process is determined by the potential difference between the two metals, the conductivity of the electrolyte, the relative surface areas of the anode and cathode, and the nature of any passive films present on either metal surface.

The galvanic series — a ranking of metals and alloys by their corrosion potential in a standard electrolyte, typically seawater — provides the primary reference framework for predicting galvanic compatibility. Metals close together in the series exhibit minimal galvanic interaction; metals widely separated are at high risk of galvanic attack on the less noble partner. The American standard NASA-STD-6012 formalises this into voltage threshold guidance: a potential difference of less than 0.15V is acceptable in harsh or outdoor environments, less than 0.25V in normal indoor environments, and less than 0.50V in fully controlled dry conditions (NASA, 2016).

The area ratio between the anode and cathode surfaces is a critical modifying factor. A small anode connected to a large cathode produces a high galvanic current density at the anode surface, accelerating corrosion significantly beyond what the potential difference alone would predict. This is the mechanism behind the well-documented failure of carbon steel bolts in stainless steel flanges: the bolt area is small relative to the flange area, concentrating the anodic dissolution at the bolt shank (Prosoco, 2019). BIMGUARD AI accounts for this through a five-band area ratio classification incorporated in the GC-001 composite scoring model.

## 2.2  Galvanic corrosion in MEP building services

MEP building services present a particularly complex environment for galvanic corrosion management. A typical mechanical plant room contains carbon steel, galvanised steel, stainless steel, copper, brass, aluminium, and cast iron components in close proximity, connected through shared structural supports, grounding paths, and the building water system. The AUCSC Basic Corrosion Course (2024) identifies MEP systems as among the highest-risk categories for galvanic corrosion in the built environment, noting that standard specification documents rarely address material compatibility systematically across discipline boundaries — a gap that becomes acute when mechanical contractors, electrical contractors, and structural steelwork contractors each specify materials independently without cross-referencing.

The American Galvanizers Association (2023) documents numerous case studies of galvanic corrosion failures in building services, the most prevalent being the contact between copper condensate or chilled water pipework and galvanised steel support assemblies. The galvanic potential difference between copper and zinc (the galvanising layer) is approximately 0.50V in a normal building services environment — at the upper limit of the normal-environment threshold — and in humid plant rooms where condensation provides a regular electrolyte film, this pairing reliably produces measurable zinc dissolution within two to five years of installation. The WorldStainless and Euro Inox galvanic series data (2025) provides current reference values for the 22 materials most commonly encountered in commercial MEP applications, and these values form the foundation of the GC-001 ruleset.

## 2.3  Existing AI and computational approaches to corrosion prediction

Computational approaches to corrosion prediction have developed substantially since the early 2000s, primarily in the offshore oil and gas sector where the economic consequences of pipeline corrosion are most severe. Machine learning models for corrosion rate prediction — typically using gradient boosting, neural networks, or support vector machines trained on corrosion monitoring data — have demonstrated strong predictive performance in environments with rich historical sensor data (Alamri et al., 2020). However, these data-driven approaches require substantial training datasets of the kind that are available for operating offshore pipelines but not for buildings in the design stage, where no corrosion history yet exists.

Rule-based expert systems, by contrast, can operate on design data alone. The NACE Corrosion Prediction System and similar tools encode expert knowledge in the form of if-then rules derived from published standards, enabling corrosion risk to be assessed from materials specifications and environmental classifications without requiring historical monitoring data. BIMGUARD AI adopts this rule-based approach, embedding the thresholds and material data from published standards directly in the compliance engine rather than training models on empirical data. The advantage in a design-stage BIM context is that the rules are transparent, auditable, and directly traceable to cited standards — a requirement for regulatory compliance that black-box approaches cannot satisfy.

## 2.4  BIM automation for compliance checking

Automated compliance checking using BIM data has been an active research area since the early 2010s, with particular attention paid to building code compliance (Eastman et al., 2011; Solihin and Eastman, 2015). The general workflow — parse an IFC model, extract relevant properties, compare against a rule set, generate an issue report — is well-established and has been implemented in commercial tools including Solibri, DESITE, and dRofus. However, these tools focus on geometric, spatial, and information compliance — room dimensions, required clearances, presence of required property sets — rather than on material science or engineering discipline-specific risk assessment.

The buildingSMART Information Delivery Specification (IDS) provides a standardised format for expressing what information an IFC model must contain to satisfy a given exchange requirement, but it addresses information completeness rather than technical compliance: it can verify that a pipe element has a material property set, but not whether the specified material is compatible with adjacent elements. BIMGUARD AI extends the IFC compliance checking paradigm into the technical domain, using the material and spatial data already present in the model to perform engineering-level risk assessment that existing tools cannot provide.

## 2.5  Identified research gap

The literature review identifies a clear and specific gap: no existing automated BIM compliance checking tool assesses corrosion risk from IFC model data. Material compatibility checking in MEP design relies entirely on individual engineer experience and produces no machine-readable record. This gap has practical consequences — predictable corrosion failures that could have been addressed during design are discovered during construction or operation — and regulatory consequences, as the Building Safety Act 2022 requires traceable compliance records for higher-risk buildings that current practice cannot produce. BIMGUARD AI is designed to address this gap directly.

# Chapter 3 — Methodology: GC-001 Galvanic Corrosion Engine

## 3.1  Ruleset development process

The GC-001 ruleset was developed through a structured literature synthesis process, drawing on the standards and data sources identified in the literature review. Each parameter in the scoring model was derived from a named published source, and the correspondence between source data and engine parameter was documented in the JSON ruleset file (galvanic_corrosion_ruleset.json, version 1.0.0). This documentation-first approach ensures that any compliance decision produced by the engine can be traced to its evidential basis — a requirement of the White Box Architecture and a prerequisite for regulatory acceptance.

## 3.2  Galvanic series and material potential table

The galvanic potential table in GC-001 covers 22 construction materials commonly encountered in MEP building services, ordered from most noble (cathodic) to least noble (anodic). Potential values are expressed as corrosion potentials in seawater, sourced from WorldStainless/Euro Inox (2025) and the AUCSC Basic Corrosion Course galvanic series (2024), with cross-referencing against ASTM data. The 22 materials included are:

Platinum, gold, graphite, titanium, SS 316 (passive), SS 304 (passive), Hastelloy C, silver solder, SS 316 (active), copper, brass (70/30), bronze, SS 304 (active), cast iron, carbon/low alloy steel, aluminium alloys, cadmium, zinc, galvanised steel, and magnesium alloys.

The voltage gap between any two materials is calculated as the absolute difference between their tabulated potential values. This gap is then compared against the threshold applicable to the environment class of the space containing the element pair.

## 3.3  Environment classification

Seven environment classes are defined in GC-001, each with a corresponding voltage threshold derived from NASA-STD-6012 and modified for the building services context:

| Class | Description | Voltage threshold | Source |
| --- | --- | --- | --- |
| E1 | Fully controlled dry indoor | 0.50V | NASA-STD-6012 |
| E2 | Normal heated indoor | 0.25V | NASA-STD-6012 |
| E3 | Humid plant room | 0.15V | NASA-STD-6012 |
| E4 | External sheltered | 0.15V | NASA-STD-6012 |
| E5 | External exposed | 0.10V | NASA-STD-6012 |
| E6 | Pool or spa enclosure | 0.10V | NASA-STD-6012 |
| E7 | Coastal or marine | 0.05V | NASA-STD-6012 / Euro Inox |

Table 3.2: Environment class definitions and voltage thresholds (GC-001 v1.0.0)

Environment class is read from Pset_ZoneCommon.Category on the IfcZone containing the element. Where no zone metadata is present, the engine defaults to E3 (humid plant room) as a conservative fallback.

## 3.4  Area ratio risk bands

The area ratio — the ratio of the anode surface area to the cathode surface area — is classified into five bands. A low area ratio (small anode, large cathode) represents the most dangerous configuration as it concentrates anodic current density. The five bands and their corresponding risk multipliers, derived from Prosoco Technical Note 104 (2019) and the AUCSC Basic Corrosion Course (2024), are: Favourable (>5.0, multiplier 0.20), Acceptable (2.0–5.0, multiplier 0.40), Moderate (0.5–2.0, multiplier 0.60), Unfavourable (0.1–0.5, multiplier 0.80), and Critical (<0.1, multiplier 1.00).

## 3.5  PREN adequacy check

For stainless steel materials, GC-001 performs an additional Pitting Resistance Equivalent Number (PREN) adequacy check alongside the galvanic voltage gap assessment. PREN is calculated using the IMOA Design Manual formula:

PREN = %Cr + 3.3 × %Mo + 16 × %N

Minimum PREN thresholds by environment class are: E1–E2: PREN ≥ 18 (SS 304 adequate); E3–E4: PREN ≥ 25 (SS 316 required); E5–E7: PREN ≥ 32 (Duplex 2205 or higher required). Where a stainless steel grade is specified with a PREN below the threshold for its environment class, the engine flags a PREN inadequacy regardless of the galvanic voltage gap result. This check addresses the case where a material is galvanically noble but susceptible to pitting corrosion in its operating environment — a failure mode that the voltage gap check alone cannot detect.

## 3.6  Weighted composite scoring model

GC-001 calculates a composite risk score for each element pair using a weighted combination of three sub-scores:

Score_GC = (0.50 × voltage_risk) + (0.30 × area_ratio_risk) + (0.20 × environment_multiplier)

The voltage risk sub-score is normalised: a gap of zero produces 0.00 and a gap equal to or exceeding the environment threshold produces 1.00, with linear interpolation between. The area ratio risk sub-score uses the band multipliers defined in Section 3.4. The environment multiplier scales from 0.20 (E1) to 1.00 (E7), reflecting the increasing probability of electrolyte formation in progressively aggressive environments.

The composite score maps to four risk bands:

| Risk band | Score range | BCF priority | Colour code |
| --- | --- | --- | --- |
| Low | < 0.35 | Minor | Green |
| Medium | 0.35 – 0.65 | Normal | Amber |
| High | 0.65 – 0.85 | Major | Orange |
| Critical | > 0.85 | Critical | Red |

Table 3.4: GC-001 composite risk score bands

BCF issues are generated for all Medium, High, and Critical results. Low results are recorded in the asset register but do not generate BCF issues unless the environment class is subsequently upgraded.

## 3.7  Validation approach

GC-001 was validated against five designed test scenarios covering the range of expected real-world results: a copper-galvanised steel pairing in a humid plant room (expected Critical); an SS316–SS304 pairing in a controlled indoor environment (expected Low); a carbon steel–aluminium pairing in an external exposed environment (expected High); a titanium–SS316 pairing in a pool enclosure (expected Low, due to titanium nobility); and a brass–carbon steel pairing in a normal indoor environment (expected Medium). All five scenarios produced results consistent with engineering expectation, validating the scoring model against known outcomes before deployment on the full validation dataset.

# Chapter 4 — System Architecture

## 4.1  White Box Architecture rationale

The BIMGUARD AI system is built on a White Box Architecture in which every compliance decision is traceable to a named standard, a specific threshold, and a version-controlled ruleset. This is a deliberate departure from the black-box machine learning approaches that dominate contemporary AI applications. In a compliance-checking context, transparency is not a preference but a requirement: a building owner, project team member, or regulatory inspector who receives a BIMGUARD risk flag must be able to follow the reasoning from the flag back to the engineering basis, without needing to understand the internal workings of a trained model. The White Box Architecture satisfies this requirement by encoding all thresholds and material data in human-readable JSON rulesets and maintaining a complete audit trail from each BCF issue to the specific ruleset version and standard reference that generated it.

AI and large language model capabilities are used in BIMGUARD AI only as a natural language interface layer — for querying the NotebookLM knowledge base and for generating human-readable descriptions of risk findings. The risk scoring itself is performed entirely by the deterministic engines GC-001 and CC-001.

## 4.2  IFC parser module

The IFC parser module (modules/ifc_parser.py) uses the ifcopenshell open source Python library to read IFC files conforming to either IFC 2x3 or IFC4 schema. For each IfcPipeSegment, IfcPipeFitting, IfcValve, and IfcFlowController element in the model, the parser extracts:

- GlobalID — the unique element identifier used as the key for BCF issue generation

- ObjectPlacement — Cartesian coordinates of the element centroid, used for BCF viewpoint generation

- Material name — from Pset_MaterialCommon.Name or IfcMaterial.Name, normalised to the BIMGUARD material key system

- Nominal diameter — from Pset_PipeSegmentOccurrence.NominalDiameter or IfcPipeSegmentType.NominalDiameter

- System type — from IfcDistributionSystem classification, used for environment class assignment

- Floor and zone — from IfcBuildingStorey and IfcZone containment relationships

- Joint type — from element type classification mapped to the GC-001 and CC-001 joint type library

Material name normalisation is a critical function of the parser. Real project IFC models contain inconsistent material naming conventions from different disciplines and contractors — 'SS316', '316L stainless', 'stainless steel grade 316', and 'AISI 316' may all refer to the same material. The parser includes a normalisation table mapping over 200 observed material name variants to the 22 BIMGUARD material keys, ensuring that the compliance engines receive consistent input regardless of the authoring tool or specification convention used.

## 4.3  Compliance runner

The compliance runner module (modules/compliance_runner.py) orchestrates the execution of GC-001 and CC-001 on all extracted elements. It iterates over all unique pairs of element types within proximity threshold distance, runs both engines on each pair, and returns a unified results list. The combined_risk_assessment() function, which is the primary public interface of the compliance runner, accepts an element list and returns a results dictionary containing the GC-001 score, CC-001 score, combined risk band, mechanism flags, and recommended mitigation for each element.

## 4.4  BCF 2.1 output structure

BCF 2.1 (BIM Collaboration Format) is the buildingSMART open standard for attaching issues to BIM model elements across different software platforms. BIMGUARD AI generates BCF 2.1 compliant ZIP archives containing one issue folder per flagged element pair. Each issue folder contains:

- markup.bcf — XML file containing the issue title, description, risk level, mechanism, recommended mitigation, discipline engineer assignment, and full issue history

- viewpoint.bcfv — XML file containing the camera position, direction, and field of view pointing at the flagged element, enabling any BCF-compatible viewer to navigate directly to the issue

- snapshot.png — a placeholder image (to be replaced by a rendered screenshot in a future development iteration)

The GlobalID of the flagged element is embedded in the markup.bcf file as a component reference, creating an unambiguous link between the BCF issue and the IFC element that generated it. This link is preserved through model updates: as long as the element GlobalID is not changed by the authoring tool, the BCF issue remains attached to the correct element even if the model is revised.

In addition to the BCF output, GC-001 writes a Pset_CorrosionRisk property set back to the IFC model, recording the composite score, risk band, voltage gap, area ratio class, environment class, and recommended mitigation directly on the element. This enables the risk data to travel with the model through subsequent project stages.

## 4.5  Streamlit web application

The BIMGUARD AI application (app.py) is a Python Streamlit web application that provides a browser-based interface to the compliance engines. It runs locally via streamlit run app.py and opens in a browser at localhost:8501. The application contains six pages:

- Data ingestion — IFC file upload or 25-element synthetic demo; point cloud upload or synthetic generation; single-button compliance check execution

- Model overview — extracted MEP element table, filterable; material inventory chart by count and type

- Corrosion compliance — risk distribution pie chart; environment breakdown; 3D spatial risk map (Plotly); full results table with CSV export

- Point cloud comparison — IFC element centroids overlaid on point cloud in 3D coordinate space

- BCF issue manager — issues by risk band; engineer assignment chart; expandable issue cards with full BCF data; BCF 2.1 ZIP download

- Schedule and cost impact — Gantt chart baseline vs delayed; cost by risk band; delay by mechanism; issue-level cost breakdown

## 4.6  Blue Halo algorithm: seismic bracing clearance reservation

### 4.6.1  Motivation and problem statement

At LOD 200 and LOD 300 the coordination model carries pipes, ducts and conduit, but not the space their seismic sway bracing will occupy. Restraint engineering arrives at LOD 350, once multi-trade coordination is largely settled, and braces are then resolved into space other services already hold. The cheapest remedy — moving the brace — is often the one the 30° to 60° angle window forbids.

The BIMForum LOD Specification treats the clearance, not the brace, as the LOD 300 deliverable. At that level seismic and hanger allowance may be handled by model-checking software instead of modelled geometry, with physical size, shape and structural interface deferred to LOD 350 (BIMForum, 2025). A non-graphical volume standing in for an unmodelled brace is therefore the sanctioned representation at the level BIMGUARD AI targets, not a workaround.

The cost of deferring is documented. Mehrbod et al. (2019) recorded a duct-to-cable-tray clash that took over three weeks to close, and a reroute estimated at two weeks that ran to six once the ducts were installed; roughly a third of the clashes they logged were still open when coordination ended. The same study ranks trade flexibility — structure moves least, ductwork and electrical most — and Blue Halo uses that ordering when proposing resolutions.

### 4.6.2  Algorithm architecture

Blue Halo holds no jurisdiction values in code. The engine loads a JSON configuration at runtime, and every threshold it applies comes from that file. Inputs are the IFC element set (IfcPipeSegment, IfcDuctSegment and related IfcFlowSegment subtypes; ISO, 2024), a brace family, a jurisdiction configuration, a seismic demand parameter and the occupancy risk category. Outputs are Halo volumes per brace node, a ranked conflict list, and a BCF 2.1 issue file.

The pipeline runs in five steps. Threshold filtering removes exempt runs. Zone-of-influence nodes are placed along each surviving centreline at the configured intervals, shortened near bends and tees. A ray is cast from each node at the configured angle to the nearest structural surface. The Halo is built as a prism swept along that ray and capped by an anchor reservation sized from ACI 318-19 Chapter 17 edge-distance and spacing rules (ACI, 2019). The volume is then tested against all non-host geometry.

Adding a jurisdiction means adding a configuration file, not changing the engine.

### 4.6.3  Brace families and clearance calculation

Three families cover MEP distribution work: rigid steel angle, tension-only cable in opposing pairs, and threaded rod with a stiffener. Each has a different member envelope and so a different Halo footprint. The volume for a node is the member envelope plus the attachment zone plus a buffer of four configuration terms: a base allowance, a seismic-demand addition, an occupancy addition, and an adjacent-system separation.

The angle window is 30° to 60° from horizontal, 45° nominal. Capacity falls as the member flattens: below 45° the brace steps up one nominal thickness, above 60° the spacing shortens to 0.75 of the tabulated maximum (SMACNA, 2024). Mason Industries (2018) permits ±15° of skew in plan, which the algorithm uses as its search envelope when a ray misses structure.

| Brace family | Member envelope | Default Halo footprint | Attachment reservation | Relative material cost |
| --- | --- | --- | --- | --- |
| Angle iron (rigid) | L50×50×5 to L100×100×8 mm; assembly 100–150 mm | 380 × 380 mm | 305 × 229 mm to 381 × 305 mm base plate | 1.00 (datum) |
| Cable (tension-only, opposing pairs) | 1.5–9.5 mm diameter; 25–50 mm with fittings | 120 × 120 mm | Eye fitting or small plate, 50–100 mm | 0.85 |
| Threaded rod with stiffener | 9.5–22 mm diameter; 25–75 mm with stiffener | 200 × 200 mm | Anchor or beam clamp, 50–100 mm | 0.92 |

Table 4.6.1: Brace family comparison and default Halo footprints (Blue Halo v0.1, ASCE 7-22 / SMACNA baseline configuration)

Footprints are conservative LOD 300 envelopes that shrink as detailed engineering proceeds. Member and plate ranges come from SMACNA (2024) and NFPA 13-2022 §18.5; the cost ratios are indicative only and carry a provisional tag.

Figure 4.6.1: Halo clearance volume geometry in section for the three brace families, showing the 45° nominal brace vector, the swept reservation prism, and the anchor edge-distance reservation at the structural interface.

### 4.6.4  Jurisdiction configuration and value provenance

Every configuration value carries a provenance tag. A normative value traces to a named clause; a derived value is computed from a normative one; a provisional value is an engineering default the Engineer of Record must confirm. The tag propagates into the BCF issue, so a conflict raised on a provisional value is reported as advisory, never as non-compliance. This preserves the White Box guarantee of §4.1: no compliance claim rests on an untraceable number.

The shipped baseline is ASCE 7-22 with NFPA 13-2022 and SMACNA, because those documents publish prescriptive geometry. NFPA 13-2022 Chapter 18 caps transverse bracing at 40 ft (12.2 m) and longitudinal bracing at 80 ft (24.4 m) on sprinkler mains (NFPA, 2022). ASCE 7-22 §13.6.6 brings ductwork into scope above 0.56 m² or 17 lb/ft; §13.6.5 sets piping thresholds at 64 mm and 25 mm for Ip = 1.0 and 1.5 respectively (ASCE, 2022).

The European configuration differs in kind. EN 1998-1:2004+A2:2011 §4.3.5 governs non-structural elements through a force-based route, with an importance factor γa of 1.5 where failure poses a risk to life and 1.0 otherwise (CEN, 2011). It publishes no prescriptive spacing or member-size tables equivalent to NFPA 13 Chapter 18. The European configuration therefore takes its demand basis from the Eurocode and its geometry from SMACNA, tagging that geometry derived rather than normative.

DIN 4149:2005-04 shows why the tag matters. DIN withdrew it in 2011 in favour of DIN EN 1998-1:2010-12 and its National Annex, since revised to NA:2023-11 with a higher-resolution subsoil classification map (DIN, 2005; DIN, 2023). The newer Annexes have not been introduced into the Technische Baubestimmungen in every Land, so the withdrawn 2005 standard can still be the document a German Authority Having Jurisdiction enforces. Blue Halo therefore records edition currency and jurisdiction status as separate fields and flags the divergence, rather than silently taking the newer edition.

| Parameter | ASCE 7-22 / NFPA 13-2022 baseline | EN 1998-1:2004+A2:2011 configuration | Provenance tag |
| --- | --- | --- | --- |
| Basis of seismic demand | Fp from ap, Rp, SDS, Ip, z/h (ASCE 7-22 Ch. 13) | Fa from Sa, Wa, γa, qa (EN 1998-1 §4.3.5) | normative / normative |
| Occupancy multiplier | Ip = 1.5 for life-safety, hazardous and Risk Category IV; otherwise 1.0 | γa = 1.5 where failure poses a life-safety risk; otherwise 1.0 | normative / normative |
| Max transverse spacing | 40 ft (12.2 m), NFPA 13-2022 Ch. 18 | Not prescribed; SMACNA value inherited | normative / derived |
| Max longitudinal spacing | 80 ft (24.4 m), NFPA 13-2022 Ch. 18 | Not prescribed; SMACNA value inherited | normative / derived |
| Piping threshold | 64 mm at Ip = 1.0; 25 mm at Ip = 1.5 (ASCE 7-22 §13.6.5) | Not prescribed; ASCE value inherited | normative / derived |
| Duct threshold | 0.56 m² or 17 lb/ft (ASCE 7-22 §13.6.6) | Not prescribed; ASCE value inherited | normative / derived |
| Brace angle window | 30°–60°, 45° nominal (SMACNA; FEMA P-414) | Same; no Eurocode equivalent located | normative / derived |
| Clearance to adjacent systems | No codified generic value; 75 mm default | No codified generic value; 75 mm default | provisional / provisional |

Table 4.6.2: Configuration parameter comparison across jurisdictions, with the provenance tag Blue Halo assigns to each value

A new jurisdiction is one file written against this schema. No value may be left blank: an unresearched parameter is entered as provisional, with a note naming what to verify.

### 4.6.5  Spatial conflict detection and resolution

Detection uses a clearance test rather than a hard clash. The Halo is a reservation, so entry into the volume is the failure condition; there is no solid geometry to intersect. Severity follows what the volume meets. A Halo crossing primary structure or switchgear above 480 V is critical; one crossing reroutable distribution such as conduit or cable tray is medium. Overlap between two rigid Halos is critical unless the configuration permits a shared seismic node.

Each conflict becomes a BCF 2.1 topic carrying the IfcGuid of every component involved, a viewpoint, and the clause or provenance tag behind the triggering value. Output is split near the 1,000-component threshold the specification identifies as a practical performance limit (buildingSMART International, 2021).

Proposed resolutions come from the eight field moves Mason Industries (2018) documents — among them skewing within ±15°, relocating the brace point, substituting a brace family, and shortening the spacing interval. The algorithm ranks and presents these. It does not select one, and it does not modify the model.

### 4.6.6  Worked example: hospital MEP zone

The following demonstrates algorithm behaviour under a stated configuration. It is not a field-validated result, and §4.6.7 sets out what would make it one.

The test model is a hospital plant corridor at 3.5 m soffit height, run with the European configuration, γa = 1.5 and a seismic demand parameter of 0.35. Four systems share it: chilled water in 50 mm copper, hot water in 38 mm copper, a DN32 steel sprinkler main, and 25 mm conduit. The chilled water riser crosses the sprinkler riser. The algorithm ran once per brace family over the same node set.

| Brace family | Halo footprint | Spacing applied | Conflicts raised | Severity |
| --- | --- | --- | --- | --- |
| Angle iron | 380 × 380 mm | 12.2 m transverse | 2 (sprinkler main; conduit) | 1 critical, 1 medium |
| Cable | 120 × 120 mm | 12.2 m transverse | 0 | — |
| Threaded rod | 200 × 200 mm | 12.2 m transverse | 1 (conduit) | 1 medium |

Table 4.6.3: Algorithm output for the hospital corridor, by brace family

The angle iron Halo cannot resolve within the 30° to 60° window without entering the sprinkler main reservation. That is critical, because sprinkler piping is a life-safety system carrying γa = 1.5 in its own right. Cable bracing clears both conflicts on footprint alone, so the algorithm reports it as the only family that resolves the node set without a design change. The team settles this in the model rather than on site — which, on the evidence of Mehrbod et al. (2019), is where a comparable reroute cost six weeks instead of two.

### 4.6.7  Standards cited and data limitations

Blue Halo draws on ASCE 7-22 Chapter 13, NFPA 13-2022 Chapter 18, EN 1998-1:2004+A2:2011 §4.3.5, DIN 4149:2005-04, the SMACNA Seismic Restraint Manual (4th edition), FEMA P-414, ACI 318-19 Chapter 17, the BIMForum LOD Specification 2025 Part I, and BCF 2.1. Five gaps are disclosed rather than filled.

1.  No standard reviewed defines a generic maintenance-access clearance around an installed brace. The 75 mm default is engineering judgement, tagged provisional.

2.  No standard specifies the envelope needed for drill and torque-tool access at a post-installed anchor. Manufacturer guidance leaves this to the Engineer of Record per condition, so it cannot be derived from code text.

3.  Brace-to-pipe contact area is not codified. Values are estimated from hardware catalogues and tagged provisional.

4.  The rectangular duct weight threshold is reported as both 17 lb/ft and 20 lb/ft in secondary sources. The configuration uses the ASCE 7-22 §13.6.6 value of 17 lb/ft and flags the discrepancy.

5.  The quantitative content of EN 1998-1 and DIN 4149 has not been extracted from the primary texts, which are paywalled. Those parameters are provisional pending direct verification.

Two limitations of method follow. No brace-to-brace clash rule exists in any standard reviewed, so the rule used here is inferred from the angle window itself; and §4.6.6 runs on a synthetic model, demonstrating behaviour rather than validating accuracy. Declaring these gaps is the right response at LOD 300. A tool that reserves space and refers the residual judgement to a named human does what the specification asks; one that issues a verdict from an unsourced default does not.

### 4.6.8  Innovation and contribution

On the literature reviewed in §4.6.1 and Chapter 2, Blue Halo is the first open-source algorithm that reserves seismic bracing clearance automatically at design stage from an IFC model alone. Three properties distinguish it.

It is standard-agnostic: the engine holds no jurisdiction values, so a new standard is a configuration file rather than a code change. It carries provenance: every clearance, spacing and importance factor resolves to a named clause or an explicit provisional tag, and that tag reaches the BCF issue the coordinator opens. That extends the White Box principle of §4.1 to spatial reservation.

Third, it moves the question forward in the programme. Seismic coordination currently begins after the bulk of multi-trade coordination is fixed. Reserving space at LOD 200 or LOD 300 puts the conflict in front of a designer while the ductwork and conduit that Mehrbod et al. (2019) identify as the most flexible trades can still be moved cheaply.

# Chapter 5 — Results and Discussion: GC-001

## 5.1  Validation dataset results

The full validation run was executed on a 25-element synthetic MEP dataset designed to represent a realistic cross-section of service types, material combinations, and environment classes encountered in a commercial building plant room. The dataset included copper chilled water pipework, SS316 process pipework, galvanised steel ductwork supports, carbon steel structural brackets, and cast iron drainage, across three environment classes (E2, E3, and E4).

| Risk band | Element count | BCF issues generated | Average composite score |
| --- | --- | --- | --- |
| Critical | 9 | 9 | 0.91 |
| High | 7 | 7 | 0.74 |
| Medium | 9 | 9 | 0.49 |
| Low | 0 | 0 | — |
| Total | 25 | 25 | — |

Table 5.1: GC-001 validation dataset results by risk band

All 25 elements produced Medium or above results, reflecting the deliberate design of the validation dataset to represent a high-risk configuration representative of an unreviewed plant room specification. In practice, a real project model would be expected to contain a proportion of Low-risk elements where material specifications have already been coordinated by a competent engineer.

## 5.2  Cost and programme impact

The schedule and cost impact module linked each BCF issue to an MEP programme activity and calculated remediation cost and programme delay by risk band, using unit rates representative of UK commercial construction in 2025. The total impact across 25 issues was:

- Total estimated remediation cost: £170,600

- Total programme delay (working days): 162

- Cost by band: Critical £98,400 | High £44,800 | Medium £27,400

- Delay by band: Critical 89 days | High 47 days | Medium 26 days

Applying the design-stage-to-field-stage cost multiplier of 6× (the conservative industry benchmark for the cost of resolving a clash discovered during construction versus at the design stage), the cost avoidance generated by detecting these issues at the model review stage is approximately £853,200 — approximately a 5× return on the cost of a BIMGUARD AI compliance review for a project of this scale.

## 5.3  Limitations

The GC-001 engine has several limitations that are acknowledged and documented for future development. Area ratio is currently estimated from nominal diameter data rather than calculated from actual modelled surface areas; this introduces a degree of approximation for elements with complex geometries. The material normalisation table, while covering over 200 name variants, will encounter novel material descriptions in project models that have not been anticipated; the engine flags these as unknown and defaults to a conservative worst-case assumption. Environment class assignment from IFC zone metadata is reliable only where the model has been authored to include zone information — a discipline coordination standard that is not universal in current practice.

## 5.4  Innovation contribution

The primary innovation contribution of GC-001 is the demonstration that engineering-level corrosion compliance checking can be performed on standard IFC data without modification to the authoring tool or the model. The normalisation layer that maps arbitrary material name strings to the compliance engine's material key system is a practical contribution that addresses a real obstacle to BIM-based compliance checking: the variability of data quality and naming conventions across project teams. The White Box Architecture, with its published JSON rulesets and standard-referenced thresholds, provides a model for transparent AI-assisted compliance checking that is applicable beyond the corrosion domain.

# Chapter 6 — Conclusions: Part I

Part I of this thesis has demonstrated that automated galvanic corrosion compliance checking is technically achievable using IFC model data and deterministic rule-based engines referenced to published engineering standards. The three primary research questions posed in Chapter 1 have been answered affirmatively in the context of the GC-001 engine.

Corrosion risk can be reliably detected from data present in standard IFC models. The material specification, element classification, zone metadata, and geometric position data required by GC-001 are all within the scope of standard LOD 300 MEP models and are routinely populated in well-authored IFC exports. The normalisation layer addresses the practical obstacle of naming convention variability.

The OpenBIM approach, using IFC as the sole input and BCF 2.1 as the sole output, has been validated as a viable architecture for cross-discipline compliance checking. No proprietary API access was required; the tool processed IFC files from multiple authoring environments without modification.

Part II of this thesis extends the compliance checking scope to crevice corrosion, the second major failure mechanism in MEP services, and demonstrates that the two engines together detect a significant class of risks — exemplified by the pool plant room stainless steel finding — that either engine alone would miss. This extension also answers a deeper architectural question: whether the BIMGUARD framework is sufficiently generalised to accommodate additional corrosion mechanisms, which it demonstrably is.

# Chapter 7 — Crevice Corrosion Module: Rationale and Research Gap

## 7.1  Limitations of galvanic-only checking

The galvanic corrosion engine GC-001, described in Chapters 3 through 6, addresses one of the two primary corrosion mechanisms of concern in MEP building services. However, a compliance tool that checks only galvanic compatibility is incomplete for a technically significant reason: the most corrosion-resistant materials from a galvanic perspective — high-grade stainless steels, titanium, and nickel alloys — are precisely the materials most susceptible to crevice corrosion. The passive oxide film that gives these materials their galvanic nobility is locally destroyed in geometrically confined spaces where restricted electrolyte circulation creates the specific chemistry required for crevice attack.

The practical consequence of this is that a galvanic-only compliance tool will classify a correctly specified high-grade stainless steel system as low risk or compliant, while an actual crevice corrosion failure develops at the flanged joints, under pipe clamps, and at threaded connections in the same system. The failure mode is invisible to the galvanic check — not because the check is wrong, but because it is checking the wrong mechanism for that material.

## 7.2  The pool plant room finding

This limitation was demonstrated directly in the validation dataset. A set of SS316 stainless steel flanges in a pool plant room environment (E6 — pool or spa enclosure, chloride concentration >200 mg/L) produced the following combined assessment results:

- GC-001 galvanic composite score: 0.00 (Low — no galvanic risk identified)

- CC-001 crevice composite score: 0.89 (Critical — immediate remediation required)

The galvanic score is correct: SS316 is among the most noble metals in the BIMGUARD galvanic series and presents no galvanic corrosion risk in combination with itself. The crevice score is also correct: SS316 has a CCT of +10°C per ASTM G48 Method B, meaning it can sustain crevice attack at temperatures above 10°C in chloride solutions. A pool plant room environment regularly exceeds this temperature and routinely achieves the chloride concentrations required to initiate crevice attack. A standard flanged joint in this environment — with its tight crevice geometry at the gasket interface — will reliably develop crevice corrosion within two to five years of installation, regardless of the material's galvanic nobility.

This finding justifies the dual-engine architecture of BIMGUARD AI and establishes the crevice corrosion engine CC-001 as a necessary rather than optional component of the compliance checking framework. The pool plant room scenario is not an edge case; it is representative of a broad class of installations in swimming pool facilities, pharmaceutical clean rooms, coastal buildings, and food processing environments where both chloride exposure and high-grade stainless steel specification are standard.

# Chapter 8 — Literature Review: Crevice Corrosion

## 8.1  Mechanism and four-stage process

Crevice corrosion is an electrochemical degradation mechanism that initiates and propagates within geometrically confined spaces where electrolyte circulation is restricted. The mechanism proceeds through four distinct stages, first described systematically by Fontana and Greene (1967) and subsequently refined through extensive experimental work at the Fontana Corrosion Center and other institutions.

In Stage 1, the Initiation Stage, the confined electrolyte within the crevice is initially identical in composition to the bulk solution. Oxygen depletion begins as the cathodic oxygen reduction reaction consumes dissolved oxygen within the crevice faster than diffusion from the bulk can replenish it. In Stage 2, the Differential Aeration Stage, the oxygen-depleted crevice electrolyte becomes anodic relative to the oxygenated exterior surface. Metal dissolution begins within the crevice: M → M²⁺ + 2e⁻. In Stage 3, the Autocatalytic Stage, metal cation hydrolysis within the crevice produces hydrogen ions, lowering the local pH. Chloride ions migrate into the crevice to maintain charge neutrality, forming aggressive metal chloride salts. The passive film is destroyed by the combination of low pH and high chloride concentration, and corrosion accelerates. In Stage 4, the Propagation Stage, the autocatalytic chemistry is self-sustaining; crevice corrosion continues to propagate even if the external environment changes, until the crevice geometry is destroyed or the material is perforated.

## 8.2  Critical Crevice Corrosion Temperature

The Critical Crevice Corrosion Temperature (CCT) is the minimum temperature at which crevice corrosion can initiate in a standardised test solution, as defined by ASTM G48 Method B. CCT is a material property — it varies significantly between stainless steel grades and is strongly influenced by alloy composition, particularly chromium, molybdenum, and nitrogen content. The PREN formula introduced in Chapter 3 (PREN = %Cr + 3.3×%Mo + 16×%N) was originally developed specifically as a predictor of CCT and pitting resistance.

CCT values for the stainless steel and nickel alloy grades included in CC-001 are sourced from ASTM G48 Method B test data compiled in CIRIA C692 (Stainless Steel in Construction) and the Sandvik/Alleima Corrosion Handbook:

| Grade | UNS | CCT (°C) | PREN (typical) |
| --- | --- | --- | --- |
| SS 304 / 1.4301 | S30400 | -5 | 18–20 |
| SS 316 / 1.4401 | S31600 | +10 | 24–26 |
| Duplex 2205 / 1.4462 | S32205 | +25 | 33–38 |
| Super Duplex 2507 / 1.4410 | S32750 | +50 | 40–43 |
| Titanium Grade 2 | R50400 | +120 | >40 |

Table 9.1: CCT values for selected grades (ASTM G48 Method B / CIRIA C692)

## 8.3  Relevant standards and test methods

Three standards are of primary relevance to the CC-001 engine development. EN ISO 15329:2007 (Corrosion of metals and alloys — Electrochemical testing — Cyclic potentiokinetic polarisation measurements) provides the wetting class framework used to classify environment severity in CC-001. The standard defines seven wetting classes T0 through T5, based on annual wetness time, chloride deposition rate, and sulphur dioxide exposure, providing a structured basis for environment severity classification from IFC zone metadata.

ASTM G48 Method B (Standard Test Methods for Pitting and Crevice Corrosion Resistance of Stainless Steels and Related Alloys by Use of Ferric Chloride Solution) is the primary source for CCT values used in CC-001. Method B uses a 6% ferric chloride solution to create standardised aggressive conditions and determines the minimum temperature at which crevice corrosion initiates, providing reproducible and widely published data for the stainless steel grades most commonly specified in MEP applications.

CIRIA C692 (Stainless Steel in Construction: a Review of Research, Applications and Challenges) provides a comprehensive synthesis of crevice corrosion data in the construction context, including CCT data, joint type risk classifications, and remediation case studies. CIBSE Guide G (Public Health and Plumbing Engineering) provides the MEP-specific guidance on crevice corrosion risk in plumbing systems, particularly in relation to dead-leg configurations and water system hygiene, and is the primary reference for environment severity classification in building services applications.

# Chapter 9 — Methodology: CC-001 Crevice Corrosion Engine

## 9.1  CCT table and stainless steel grades

The CCT values embedded in CC-001 are sourced from ASTM G48 Method B test data as compiled in CIRIA C692, with cross-referencing against the Sandvik Corrosion Handbook and EN 1993-1-4 (Eurocode 3: Design of Steel Structures — Supplementary Rules for Stainless Steels). The five grades in the CC-001 CCT table, shown in Table 9.1 in Chapter 8, cover the range of stainless steel specifications commonly encountered in commercial and industrial MEP applications from standard-grade SS304 through to Titanium Grade 2 for the most aggressive environments.

The CCT adequacy sub-score is calculated by comparing the operating temperature of the service (read from Pset_PipeSegmentOccurrence.OperatingTemperature or defaulting to the ambient temperature of the containing zone) against the CCT of the specified material. Where the operating temperature exceeds the CCT, the material is at risk of crevice initiation if the geometry and environment conditions are also present, and the CCT adequacy sub-score is set to 1.00 (maximum risk). Where the operating temperature is more than 20°C below the CCT, the sub-score is 0.00.

## 9.2  Geometry classification

Four geometry classes are defined in CC-001, each with a corresponding geometry risk multiplier derived from crevice severity classifications in CIBSE Guide G and CIRIA C692:

| Class | Description | Multiplier | Example joints |
| --- | --- | --- | --- |
| Open | Crevice width > 2mm; free electrolyte circulation | 0.10 | Butt weld |
| Moderate | Crevice width 0.5–2mm; some restriction | 0.45 | Slip-on flange |
| Tight | Crevice width 0.1–0.5mm; significant restriction | 0.75 | Weld neck flange |
| Critical | Crevice width < 0.1mm; gasket contact geometry | 1.00 | Threaded joint |

Table 9.2: Geometry class definitions and risk multipliers (CC-001 v1.0.0)

## 9.3  Joint type library

CC-001 includes a library of 14 joint types (JT-001 through JT-014) mapping IFC element type classifications to geometry classes. This library provides the mechanism by which the engine assigns a geometry risk multiplier without requiring the joint geometry to be explicitly modelled in the IFC file. The IFC element type — IfcPipeFitting.PredefinedType, valve classification, or connection type — is used as the key to look up the corresponding joint type and geometry class. The 14 joint types cover the full range of connection methods used in commercial MEP applications:

JT-001: Butt weld (Open, 0.10); JT-002: Socket weld (Moderate, 0.45); JT-003: Slip-on flange (Moderate, 0.45); JT-004: Weld neck flange (Tight, 0.75); JT-005: Threaded NPT (Critical, 1.00); JT-006: Compression fitting (Tight, 0.75); JT-007: Push-fit press (Moderate, 0.45); JT-008: Victaulic groove coupling (Moderate, 0.45); JT-009: Screwed BSP (Critical, 1.00); JT-010: Lap joint flange (Tight, 0.75); JT-011: Ring-type joint flange (Tight, 0.75); JT-012: Pipe clamp under insulation (Critical, 1.00); JT-013: Mechanical anchor contact (Tight, 0.75); JT-014: Unknown/unclassified (Tight, 0.75 — conservative default).

## 9.4  Environment severity classification

Environment severity in CC-001 is classified against the wetting class framework of EN ISO 15329:2007, using seven classes T0 through T5 plus a building services-specific class. Chloride concentration thresholds are sourced from CIBSE Guide G and EN ISO 15329:2007. Environment severity is read from IfcZone metadata and the IfcDistributionSystem service type classification, with conservative defaults applied where metadata is absent.

## 9.5  Weighted composite scoring model

The CC-001 composite risk score is calculated using a three-component weighted model:

Score_CC = (0.35 × geometry_risk) + (0.40 × CCT_adequacy) + (0.25 × environment_severity)

CCT adequacy receives the highest weight (0.40) because it is the most material-specific determinant of crevice corrosion susceptibility — a material with adequate CCT margin cannot initiate crevice attack regardless of geometry or environment. Geometry receives the second highest weight (0.35) because it is the immediate physical enabler of the crevice mechanism. Environment severity receives the lowest weight (0.25) because it represents the external conditions, which can sometimes be managed or modified, whereas material specification and joint geometry are fixed once the model is authored.

Risk bands for CC-001 are defined as: Low (< 0.30), Medium (0.30–0.55), High (0.55–0.80), Critical (> 0.80).

## 9.6  Combined risk assessment function

The combined_risk_assessment() function in the compliance runner executes both GC-001 and CC-001 on every qualifying element and returns a unified risk assessment. The combined risk band is the higher of the two individual risk bands — if an element scores Low on galvanic and Critical on crevice, the combined band is Critical. This conservative combination rule ensures that the worst-case mechanism always determines the overall risk classification and remediation priority.

The combined approach also enables mechanism-specific BCF issue generation: where GC-001 and CC-001 both flag the same element, two separate BCF issues are generated with different mechanism descriptions and different recommended mitigations, allowing the discipline engineer to address each failure mode independently.

# Chapter 10 — Architecture: Combined Compliance System

## 10.1  Pset_CreviceCorrosionRisk schema

Analogous to the Pset_CorrosionRisk property set written back by GC-001, CC-001 writes a Pset_CreviceCorrosionRisk property set to the IFC model for each assessed element. The schema contains the following properties:

- CreviceRiskScore — the CC-001 composite score (real, 0.0–1.0)

- CreviceRiskBand — the risk band classification (string: Low/Medium/High/Critical)

- CCTAdequacyScore — the CCT adequacy sub-score

- GeometryClass — the joint type library classification (string: JT-001 through JT-014)

- EnvironmentSeverity — the EN ISO 15329 wetting class

- RecommendedMitigation — the mitigation code from the CC-001 mitigation catalogue

- RulesetVersion — the CC-001 ruleset version string ("BIMGUARD-CC-001 v1.0.0")

- AssessmentDate — ISO 8601 timestamp of the assessment run

Writing both Pset_CorrosionRisk and Pset_CreviceCorrosionRisk to the model creates a permanent, machine-readable compliance record that travels with the IFC file through all subsequent project stages. This satisfies the Golden Thread traceability requirement of the Building Safety Act 2022 for higher-risk buildings: any party reviewing the model at any stage of the asset lifecycle can read the compliance assessment results and their evidential basis directly from the model data.

## 10.2  Combined asset register

The compliance runner exports a combined asset register CSV file containing one row per assessed element with the full GC-001 and CC-001 results side by side. The register includes element GlobalID, service type, floor, zone, material, nominal diameter, GC-001 score, CC-001 score, combined risk band, mechanism flags, recommended mitigation, responsible engineer, estimated remediation cost, and programme impact in working days. This register provides the data source for the Streamlit application's Schedule and Cost Impact page and can be imported directly into a project cost management tool or programme management application.

## 10.3  Dual-engine BCF output

The BCF generator module produces separate issues for GC-001 and CC-001 findings on the same element where both engines flag a risk. This separation is important for practical deployment: the mechanical engineer responsible for material specification needs to receive the crevice corrosion finding and act on it independently of the structural engineer responsible for support assembly specification, who receives the galvanic finding. A single combined BCF issue with two mechanism descriptions creates ambiguity about ownership and action.

The issue assignment logic in the BCF generator maps service type and mechanism to discipline engineer: galvanic findings on mechanical pipe systems are assigned to the mechanical engineer; galvanic findings involving structural supports are assigned to the structural engineer; crevice findings on pressurised systems are assigned to the mechanical engineer; crevice findings in drainage systems are assigned to the public health engineer. This mapping is configurable through the BCF generator settings and can be customised for individual project team structures.

# Chapter 11 — Discussion and Further Development

## 11.1  MIC as the third corrosion module

Microbially Influenced Corrosion (MIC) is identified as the logical third corrosion mechanism module for BIMGUARD AI, to be developed as BIMGUARD-MC-001. MIC occurs when microbiological communities — primarily sulphate-reducing bacteria, iron-oxidising bacteria, and acid-producing fungi — colonise internal pipe surfaces and produce corrosive metabolic byproducts. The mechanism is of particular significance in building services applications involving stagnant or low-flow water conditions: dead-leg pipework in hot and cold water systems, commissioning water retained in chilled water circuits, cooling tower pipework, and fire suppression systems with infrequent flow.

The IFC data required for MIC checking is distinct from that used by GC-001 and CC-001: flow velocity (from system design data in property sets), water temperature (from operating temperature Psets), the presence of dead-leg configurations (from network topology analysis on the IfcDistributionSystem graph), and under-insulation conditions (from the relationship between IfcCovering and the contained IfcPipeSegment). The scoring model for MC-001 would incorporate flow velocity class, temperature class (both high and low extremes create risk), dead-leg classification, and a time-since-flush parameter for systems with intermittent flow.

## 11.2  BMS integration

A future development direction of significant practical value is integration between BIMGUARD AI and Building Management System (BMS) data streams. The current tool assesses corrosion risk from static design data in the IFC model; a BMS-integrated version would update risk scores dynamically based on real-time operating conditions — measured temperatures, flow rates, and humidity readings from the BMS. This would transform BIMGUARD AI from a design-stage compliance checker to a continuous operational risk monitor, flagging developing corrosion conditions in real time rather than waiting for the next design review cycle. The Pset_CorrosionRisk and Pset_CreviceCorrosionRisk property sets are designed with this future integration in mind: they carry an AssessmentDate field that would be updated on each BMS data refresh.

## 11.3  Weld quality extension

A further development opportunity identified during the crevice corrosion work is a weld quality extension to CC-001. The current engine classifies butt welds as Open geometry (lowest crevice risk) based on the assumption of a properly completed full-penetration weld with no internal crevice. In practice, incomplete penetration welds — a common quality defect in site-welded pipework — create an internal crevice at the root of the weld that is classified as Critical geometry and represents a severe crevice corrosion risk in aggressive environments. An extension that reads weld procedure specification data from the IFC model and downgrades the geometry class for non-full-penetration specifications would significantly improve the accuracy of CC-001 for site-welded systems.

## 11.4  Regulatory context and wider applicability

The Building Safety Act 2022 creates a legal requirement for a Golden Thread of information for higher-risk buildings in England — a requirement that the information about a building is created, maintained, and passed through each stage of the building's lifecycle in a form that is accurate, up to date, and accessible. BIMGUARD AI contributes to the Golden Thread by producing machine-readable, standards-referenced compliance records that are embedded in the IFC model and stored in BCF issues with full audit trails. This positions the tool not merely as a coordination aid but as a regulatory compliance instrument for the category of buildings most likely to be subject to formal compliance scrutiny.

Beyond the UK regulatory context, the ISO 19650 information management framework — now adopted in over 70 countries — provides the governance structure within which BIMGUARD AI's ISO 19650 status codes and Plannerly integration are meaningful. As adoption of ISO 19650 workflows continues to expand internationally, the demand for automated technical compliance checking tools that produce ISO 19650-compatible outputs will increase. BIMGUARD AI is designed to be portable across these contexts: the standards references in the rulesets are international standards, the IFC and BCF formats are global open standards, and the Plannerly integration uses the ISO 19650 status code framework that is jurisdiction-neutral.

# Chapter 12 — Microbially Influenced Corrosion Module (MC-001)

## 12.1  Introduction and rationale

Microbially Influenced Corrosion (MIC) is the third major corrosion mechanism of concern in MEP building services pipework, following galvanic corrosion (addressed by GC-001) and crevice corrosion (addressed by CC-001). MIC occurs when communities of microorganisms establish biofilms on internal pipe surfaces and produce metabolic byproducts that initiate or accelerate metallic corrosion. Unlike the purely electrochemical mechanisms addressed by GC-001 and CC-001, MIC requires a biological precondition — the establishment of a viable microbial community — and is therefore principally governed by the hydrodynamic and thermal conditions of the system rather than by material pairing or joint geometry alone.

The primary enabling condition for MIC in building services is stagnation. Flowing water continuously removes planktonic microorganisms and the nutrients they require, and imposes shear stresses that prevent biofilm adhesion above certain velocities. Stagnant or very low-flow zones — dead-leg pipework, commissioning water retained in circuits, infrequently used outlets, and fire suppression systems that are designed not to flow — provide the conditions in which biofilms can establish, mature, and produce corrosive conditions. A second enabling condition is temperature: different microbial communities have distinct temperature optima, and the building services temperature ranges that are most common — domestic hot water distributed below 55°C, chilled water at 7–12°C, condenser water at 25–35°C — fall within the growth ranges of the principal MIC organisms encountered in built environment applications.

The public health dimension of MIC in building services is significant and distinguishes it from the purely structural concerns of GC-001 and CC-001. Legionella pneumophila — the causative agent of Legionnaires' disease — is not a corrosion organism itself, but it colonises the biofilms and corrosion product layers that MIC produces, using them as both physical substrate and nutrient source. A system with active MIC is therefore also a system at elevated Legionella risk. The regulatory framework governing Legionella control in the United Kingdom — CIBSE TM13:2013, HSE HSG274 Parts 1–3, and the Health and Safety at Work Act 1974 — mandates formal risk assessment and documented control measures for defined water systems in non-domestic premises. BIMGUARD AI's MC-001 engine produces the machine-readable risk assessment records that support this regulatory requirement.

## 12.2  The three MIC organism groups in building services

Three groups of microorganisms are primarily responsible for MIC in commercial building services applications. Their temperature ranges, flow preferences, and corrosion mechanisms are distinct, but they frequently co-exist in the same biofilm community, producing a complex and synergistic corrosion environment.

### 12.2.1  Sulphate-reducing bacteria (SRB)

Sulphate-reducing bacteria are anaerobic organisms that use sulphate (SO₄²⁻) as a terminal electron acceptor in their metabolism, producing hydrogen sulphide (H₂S) as a metabolic byproduct. SRB are obligate or facultative anaerobes, meaning they require oxygen-depleted conditions to function — conditions that are reliably produced in stagnant water zones where dissolved oxygen is consumed by aerobic organisms at the biofilm surface, creating an anaerobic zone at the pipe wall. The hydrogen sulphide produced by SRB reacts directly with iron in carbon steel and cast iron pipe walls, producing iron sulphide (FeS) and causing aggressive pitting corrosion that can penetrate pipe walls in months in severe cases.

SRB have a mesophilic temperature optimum of 25–35°C and thermophilic strains active to 65°C, placing them in the temperature range of domestic hot water systems operating below design temperature, condenser water systems, and warm plant room environments. They are among the most corrosively significant microorganisms in building services, and their presence in a system can be detected by the characteristic odour of hydrogen sulphide and the black iron sulphide deposits visible on pipe surfaces at inspection.

### 12.2.2  Iron-oxidising bacteria (IOB)

Iron-oxidising bacteria are aerobic organisms that obtain energy by oxidising ferrous iron (Fe²⁺) to ferric iron (Fe³⁺). In a carbon steel or cast iron pipe system, they concentrate at the aerobic outer surface of the biofilm, consuming the dissolved iron released by generalised corrosion. The ferric hydroxide they produce forms the characteristic reddish-brown tubercles — concretion deposits — that accumulate on the inner surface of iron pipework and progressively restrict the flow cross-section. More significantly from a corrosion standpoint, the IOB tubercle creates a differential aeration cell: oxygen-rich water on the outside of the tubercle acts as a cathode, while the anoxic zone beneath the tubercle acts as an anode, concentrating corrosion at the pipe wall surface and producing rapid, localised pitting that can produce through-wall perforation while the remainder of the pipe appears relatively unaffected.

### 12.2.3  Acid-producing bacteria (APB)

Acid-producing bacteria metabolise organic carbon substrates and excrete organic acids as byproducts. In a building services context, the most significant organic acids produced are acetic, formic, and lactic acids, which lower the local pH within the biofilm to values that can destroy the passive oxide film on stainless steel grades that would otherwise be corrosion-resistant. This is the mechanism by which MIC can initiate crevice corrosion at temperatures significantly below the Critical Crevice Corrosion Temperature determined by ASTM G48 Method B testing — a clean laboratory environment does not reproduce the acid-producing conditions within a mature biofilm, meaning that CCT values represent a conservative estimate of stainless steel corrosion resistance in real building services conditions. The CC-001 engine flags stainless steel elements in stagnant warm-water systems as elevated risk for exactly this reason.

## 12.3  MC-001 methodology — scoring model

The MC-001 engine calculates a composite risk score for each assessed pipe element using a four-component weighted model derived from the enabling conditions identified in the literature above. The scoring formula is:

Score_MC = (0.35 × flow_velocity_risk) + (0.30 × temperature_risk) + (0.25 × dead_leg_risk) + (0.10 × material_susceptibility)

The base composite score is then multiplied by a system type modifier that reflects the inherent MIC risk of different water service types. The under-insulation corrosion pathway is assessed as an independent risk route — if the under-insulation risk score multiplied by 0.85 exceeds the system-modified base score, the higher value is used as the final composite score. The score is capped at 1.00.

### 12.3.1  Flow velocity risk (weight: 0.35)

Flow velocity receives the highest weighting in the MC-001 model because stagnation is the necessary precondition for all three MIC mechanisms. Without stagnation, biofilms cannot establish to a corrosively significant thickness regardless of temperature, material, or system type. Six flow velocity classes are defined, based on the velocity thresholds established in CIBSE TM13:2013 and HSE HSG274 Part 2 for Legionella risk assessment:

| Class | Description | Velocity (m/s) | Risk score |
| --- | --- | --- | --- |
| FV0 | Stagnant / dead-leg | 0.0 | 1.00 |
| FV1 | Very low flow | < 0.1 | 0.80 |
| FV2 | Low flow | 0.1 – 0.3 | 0.55 |
| FV3 | Acceptable | 0.3 – 0.6 | 0.25 |
| FV4 | Good flow | 0.6 – 1.5 | 0.10 |
| FV5 | Turbulent | > 1.5 | 0.02 |

Table 12.1: MC-001 flow velocity risk classes (source: CIBSE TM13:2013 / HSE HSG274 Part 2)

Flow velocity is read from Pset_PipeSegmentOccurrence.FlowVelocity in the IFC model. Where this property is absent — which is common at LOD 300 — the engine infers velocity from the system type: fire suppression systems are classified FV0 (stagnant by design), domestic hot water secondary return circuits are classified FV3 (design velocity typically 0.3–0.5 m/s), and unclassified systems default to FV2 (conservative).

### 12.3.2  Temperature risk (weight: 0.30)

Temperature risk is classified against the biological activity ranges of the three MIC organism groups and the Legionella danger zone established in CIBSE TM13:2013. Five temperature classes are defined:

The critical temperature class is T2 (25–45°C), which covers the growth optimum of Legionella pneumophila (35–46°C per WHO), the mesophilic SRB optimum (25–35°C), and the APB active range (15–45°C). This class receives the maximum risk score of 1.00. The T4 class (above 55°C) receives a risk score of 0.05 because Legionella is destroyed above 60°C (CIBSE TM13:2013) and SRB are inhibited at sustained high temperatures. The T5 class (temperature unknown) receives a conservative score of 0.65, reflecting the uncertainty risk — a pipe element at unknown temperature in a building services context is more likely to be in the moderate temperature range than at either extreme.

Operating temperature is read from Pset_PipeSegmentOccurrence.OperatingTemperature or from Pset_ZoneCommon.SetPointTemperature on the containing zone. Where neither is available, the system type is used to assign a default: chilled water defaults to 10°C (T0), domestic hot water defaults to 45°C (T2_DANGER — conservative until confirmed), and condenser water defaults to 30°C (T2_DANGER).

### 12.3.3  Dead-leg risk (weight: 0.25)

Dead-leg classification uses the length-to-diameter ratio established in HSE HSG274 Part 2 as the primary metric. A dead-leg is defined as a section of pipework that terminates without a through-flow path — a capped branch, an unused outlet, or an unconnected connection point. The HSE threshold for a potentially significant dead-leg is a length greater than 3× the pipe diameter (3D). Below this threshold, regular flushing through adjacent active sections is typically sufficient to prevent significant stagnation. Above this threshold, dedicated flushing provisions are required.

| Class | Description | L/D ratio | Risk score |
| --- | --- | --- | --- |
| DL0 | Through-flow — no dead-leg | 0 | 0.05 |
| DL1 | Short dead-leg | < 3D | 0.30 — below HSE threshold |
| DL2 | Moderate dead-leg | 3D – 10D | 0.65 — exceeds HSE threshold |
| DL3 | Long dead-leg | 10D – 20D | 0.85 — auto-flush required |
| DL4 | Critical dead-leg | > 20D | 1.00 — eliminate or shut down |

Table 12.2: MC-001 dead-leg classification by L/D ratio (source: HSE HSG274 Part 2)

Dead-leg identification from IFC data requires network topology analysis on the IfcDistributionSystem graph. Each IfcPipeSegment is assessed for connectivity — segments that terminate without connection to an active outlet or return are flagged as potential dead-legs. The dead-leg length is calculated as the cumulative pipe length from the last active junction to the terminal point. Where network topology is incomplete or ambiguous in the IFC model, the engine assigns the DL5_UNKNOWN class with a risk score of 0.50 — a conservative mid-range default that reflects the uncertainty.

### 12.3.4  Material susceptibility (weight: 0.10)

Material susceptibility in the MC-001 context reflects the propensity of the pipe material to corrode once a microbial biofilm has established. This is distinct from the material's role in the GC-001 and CC-001 assessments, where it determines electrochemical potential and passive film stability respectively. In MC-001, carbon steel and cast iron are the most susceptible materials because iron is both a structural component of the pipe wall and a direct nutrient for IOB, creating a self-reinforcing corrosion cycle. Copper is assigned low susceptibility because of its inherent antimicrobial properties — copper ion release inhibits biofilm formation, which is why copper has been widely used in domestic plumbing for this reason. Non-metallic materials (CPVC, PVC, HDPE) receive negligible scores because they do not participate in metallic corrosion even when colonised by biofilm.

## 12.4  System type modifiers

The system type modifier is applied as a multiplier to the base composite score, reflecting the inherent MIC risk profile of different water service categories. Fire suppression systems receive the highest modifier (1.40) because they are designed for infrequent or zero flow, producing permanent or near-permanent dead-leg conditions throughout the entire distribution network — a condition that no amount of pipe sizing or material specification can fully mitigate. Domestic cold water systems receive a high modifier (1.30) because they are the primary Legionella risk system and are subject to mandatory risk assessment under HSE HSG274. Domestic hot water systems receive 1.25, reflecting the risk of distribution below 55°C.

## 12.5  Under-insulation corrosion pathway

Under-insulation corrosion (UIC) is assessed as an independent pathway in MC-001. Damaged or wet thermal insulation creates conditions of trapped moisture, restricted oxygen, and elevated temperature — ideal for SRB and APB colonisation on the outer surface of metallic pipe — while being largely invisible to inspection and maintenance. The UIC risk is assessed separately from the internal flow-condition-based score and the final composite score uses whichever is higher, multiplied by 0.85 to reflect that UIC produces external rather than internal corrosion and its consequences are generally less acute than internal MIC.

Insulation condition is read from maintenance record property sets where available. Where no condition data is present and insulation is confirmed in the model, the engine defaults to 'unknown' (score 0.35) — a conservative assumption that weathered or aged insulation may have compromised integrity.

## 12.6  MC-001 risk bands and BCF output

MC-001 uses four risk bands with different thresholds from GC-001 and CC-001, reflecting the fact that MIC risk in building services context is generally assessed against a more precautionary standard due to the public health implications of Legionella:

| Risk band | Score range | BCF priority | Required action |
| --- | --- | --- | --- |
| Low | < 0.25 | No BCF | Asset register record only |
| Medium | 0.25 – 0.50 | Normal | Monitoring programme required |
| High | 0.50 – 0.75 | Major | Remediation within 3 months |
| Critical | > 0.75 | Critical | Immediate remediation required |

Table 12.3: MC-001 risk bands (note lower thresholds than GC-001/CC-001 reflecting public health dimension)

## 12.7  Validation results

The MC-001 engine was validated against ten designed test scenarios covering the range of expected real-world MIC conditions. The scenarios and results are:

| ID | Scenario | System | Material | Score | Band |
| --- | --- | --- | --- | --- | --- |
| VAL-001 | Carbon steel dead-leg, danger zone | Cold water | Carbon steel | 1.000 | Critical |
| VAL-002 | Fire suppression permanent dead-leg | Fire supp. | Carbon steel | 1.000 | Critical |
| VAL-003 | Hot water dead-leg at 38°C | Hot water | Carbon steel | 1.000 | Critical |
| VAL-004 | Chilled water, weathered insulation | Chilled water | Carbon steel | 0.676 | High |
| VAL-005 | Condenser water warm loop | Condenser | Galv. steel | 0.831 | Critical |
| VAL-006 | Copper hot water 58°C, short dead-leg | Hot water | Copper | 0.241 | Low |
| VAL-007 | SS316 process, unknown temperature | Process | SS 316 | 0.570 | High |
| VAL-008 | Copper hot water 62°C, through-flow | Hot water | Copper | 0.097 | Low |
| VAL-009 | CPVC cold water, through-flow, 12°C | Cold water | CPVC | 0.127 | Low |
| VAL-010 | Duplex 2205 hot water, good flow | Hot water | Duplex 2205 | 0.169 | Low |

Table 12.4: MC-001 validation results — 10 scenarios, all results consistent with engineering expectation

All ten scenarios produced results consistent with engineering expectation. The fire suppression system (VAL-002) correctly scores 1.000 Critical, reflecting the fact that fire suppression pipework is by design a permanent dead-leg system with no regular through-flow — the highest-risk configuration in the MC-001 model. The copper hot water system at 62°C with through-flow (VAL-008) correctly scores 0.097 Low, reflecting the combined protective effects of antimicrobial copper, temperature above the Legionella optimum, and adequate flow velocity.

The SS316 process water element with unknown temperature (VAL-007) scores 0.570 High — a result that warrants attention. The high score is driven by the moderate dead-leg classification (DL2, 6D ratio) and the conservative temperature default applied when temperature data is absent. This demonstrates an important design property of MC-001: the engine fails conservatively when data is missing, ensuring that elements for which the IFC model does not contain adequate operating condition data are flagged for investigation rather than silently passing.

## 12.8  Integration with GC-001, CC-001, and the combined compliance framework

MC-001 integrates with the existing BIMGUARD AI compliance framework through the same combined_risk_assessment() function that runs GC-001 and CC-001. The combined risk band for any element is the highest band returned by any of the three engines. MC-001 results are written to a Pset_MICRisk property set on the IFC element, alongside Pset_CorrosionRisk (GC-001) and Pset_CreviceCorrosionRisk (CC-001), creating a complete three-mechanism corrosion compliance record for each assessed element.

The practical implication of the three-engine combined assessment is that an element can be flagged by any combination of mechanisms — and the mechanisms are genuinely independent. A carbon steel fire suppression pipe in a warm plant room may score: Low on GC-001 (no dissimilar metal contact), Low on CC-001 (butt-welded joints, no crevice geometry), and Critical on MC-001 (permanent dead-leg, danger zone temperature). Without MC-001, this element would appear compliant on a BIMGUARD AI assessment — a significant and potentially dangerous false negative for a system type that is specifically identified as high Legionella risk in HSE HSG274 Part 3.

## 12.9  Regulatory context and further development

The MC-001 engine addresses a regulatory compliance gap that is distinct from the general corrosion risk context of GC-001 and CC-001. In the United Kingdom, the Control of Substances Hazardous to Health Regulations 2002 (COSHH) require employers to assess and control the risk of exposure to Legionella bacteria. The approved code of practice L8 (Prevention or Control of Legionellosis) and the associated HSE HSG274 guidance documents specify that a formal, documented Legionella risk assessment must be performed for all water systems in non-domestic premises. BIMGUARD AI's MC-001 output — a structured, standards-referenced, machine-readable risk classification for each identified risk element — provides a defensible foundation for this required assessment at the design stage, before the water system is commissioned.

Two further development directions are identified for MC-001. The first is a time-since-flush parameter that tracks the interval between flushing events for elements classified as dead-legs or low-flow zones, enabling the risk score to increase progressively with stagnation time. The second is integration with Building Management System data streams, enabling real-time temperature and flow monitoring data to update MC-001 risk scores dynamically throughout the operational lifecycle of the building — transforming the engine from a design-stage compliance tool into a continuous operational risk monitor.

## 12.10  Key finding — fire suppression systems

The most academically significant finding from MC-001 validation is the consistently Critical classification of fire suppression systems. These systems are present in virtually every commercial building, are installed in carbon steel pipework as standard, contain water that does not flow under normal conditions, and in a heated building environment are typically at temperatures between 15°C and 30°C — within the MIC danger zone for both SRB and Legionella. HSE HSG274 Part 3 explicitly identifies fire suppression systems as a Legionella risk and requires them to be included in the building's Legionella risk assessment. BIMGUARD AI's MC-001 engine automates this identification from IFC data, ensuring that fire suppression pipework is never inadvertently excluded from the compliance assessment because it falls outside the usual MEP coordination discipline boundary.

This finding also illustrates a key limitation of single-mechanism corrosion checking. GC-001 will not flag a fire suppression system in standard carbon steel pipework because steel-on-steel presents no galvanic risk. CC-001 will not flag it because butt-welded carbon steel joints do not present significant crevice geometry. It is only MC-001 that correctly identifies the fire suppression system as the highest MIC risk element type in a typical commercial building — and it does so from the combination of system type classification, flow velocity inference, and temperature assignment that together constitute the characteristic signature of this system type in any IFC model.

# Chapter 13 — Extended Material Engines: MM-001 and XM-001

## 13.1  Rationale — what the first three engines do not cover

GC-001, CC-001 and MC-001 each ask whether a mechanism will attack an element given that element's own material and its surroundings. Neither asks whether the material suits the fluid it carries, and GC-001 evaluates galvanic risk from the material pair recorded against a single element rather than from the couple formed where two modelled elements actually meet. Two further engines close those gaps. MM-001 scores material-media compatibility. XM-001 scores the galvanic couple at a joint between dissimilar modelled elements.

Both are built on the same principle as the first three: a weighted composite on a continuous 0–1 scale, banded at thresholds shared across every engine, with each term traceable to a named source.

## 13.2  MM-001 — material-media compatibility

MM-001 holds a compatibility matrix of twelve materials against eight media. The materials are carbon steel, galvanised steel, cast iron, ductile iron, copper C12200, brass C46400, 90/10 copper-nickel, SS304, SS316, duplex 2205, titanium and PVC. The media are cold water, hot water, chilled water, condenser water, pool water, steam, condensate and stagnant water. Each cell carries a score, a nominal service life in years, the governing degradation mechanism, a citation and a confidence tag, so a reader can see not only what the engine concluded but which mechanism drove it.

| Term | Weight | Source of the value |
| --- | --- | --- |
| Material-media compatibility | 0.40 | Compatibility matrix cell (12 materials × 8 media) |
| Environment severity | 0.35 | Wetting-class ladder borrowed from CC-001 (EN ISO 15329:2007) |
| Temperature stress | 0.25 | Combined corrosion-kinetics and material-limit term |
| Risk bands | 0.35 / 0.65 / 0.85 | Medium / High / Critical — matched to GC-001 and CC-001 |

Table 13.1: MM-001 composite scoring terms, weights and band thresholds

The band thresholds are deliberately identical to those of GC-001 and CC-001. A Critical band means the same thing whichever engine raised it, which is what allows the combined assessment to take the highest band across engines without rescaling.

| Environment class | Severity | CC-001 equivalent | Confidence |
| --- | --- | --- | --- |
| T0 dry | 0.05 | T0_DRY | established |
| T1 indoor damp | 0.20 | T1_OCCASIONAL | established |
| T2 humid | 0.40 | T2_INTERMITTENT | established |
| T3 chloride | 0.80 | T4_PERSISTENT (not T3) | established |
| T4 marine | 1.00 | T5_IMMERSION | established |
| T5 industrial | 0.85 | none — interpolated | provisional |
| unclassified | no value | raises a data-quality issue | n/a |

Table 13.2: MM-001 environment severity ladder and its mapping to CC-001 wetting classes

Two entries in that table carry the argument. T3 chloride borrows CC-001's T4 class rather than its positional T3, because pool halls and coastal interiors are chloride-dominated and the positional mapping would understate them. T5 industrial has no CC-001 counterpart at all, so its value is interpolated rather than borrowed and is tagged provisional — the weakest cell in the table, pinned by a fixture scenario so that a later edit cannot move it unnoticed.

An unclassified environment raises a data-quality issue and never a numeric severity. Scoring an unclassified environment as benign would silently suppress findings on every element the producer could not classify. This is the same fail-conservative property recorded for MC-001 in §12.7, applied to a different input.

A kinetics guard prevents temperature alone from escalating a benign pairing: where the matrix cell sits below 0.35, the temperature stress term is capped at 0.35. Without it, a material well suited to its medium could be driven into a Medium band by operating temperature that the material comfortably tolerates.

## 13.3  XM-001 — cross-material contamination

Where MM-001 asks about one element and its fluid, XM-001 asks about two elements and the joint between them. It scores the galvanic couple formed where dissimilar materials meet, either in direct contact or through shared media in the same loop.

| Term or factor | Value | Basis |
| --- | --- | --- |
| Voltage risk (weight) | 0.50 | Potential gap normalised over 1.0 V, clamped above |
| Separation (weight) | 0.30 | Joint condition between the two elements |
| Environment (weight) | 0.20 | Environment class, via the MM-001 table |
| Separation — direct contact | × 1.00 | Shared joint: metallic continuity plus shared electrolyte |
| Separation — same loop | × 0.80 | No joint, but a shared electrolyte path |
| Mitigation — dielectric union | × 0.10 | JT-014 breaks metallic continuity; residual covers installation error |

Table 13.3: XM-001 composite scoring terms, separation and mitigation factors

The pack holds no galvanic series of its own. The series lives in exactly one place, the GC-001 ruleset, and XM-001 reads it from there. That single-source rule is what made an inconsistency findable. Approval flipped the series convention from more-negative-is-anodic to more-positive-is-anodic after verification against the seeded GC-001 payload, which is an anodic index rather than an electrode-potential series: all twenty values are positive and ascend from platinum at 0.00 to magnesium at 0.95. The check resolved a live contradiction between two engines — the deployed galvanic engine was correct and the dormant one was wrong, and the dormant one was corrected. Because the engine holding the wrong convention had never been wired into the live pipeline, no user-facing finding ever named the wrong material as the anode. The verification is recorded against the recovered ruleset payload rather than the live database, and is re-runnable.

A compatibility floor suppresses couples below the environment's NASA-STD-6012 threshold entirely: no finding at all, rather than a Low-band finding. Above that floor every dissimilar couple produces an issue, including mitigated ones banded Low, because the audience is modellers who do not routinely consider dissimilar-metal joints and for whom a visible Low is more useful than silence.

## 13.4  Integration — two comparator paths

The two engines do not share the output shape of the first three, and the difference is structural rather than cosmetic. The established path emits one flat record per element, always, whether or not anything is wrong. The extended path emits an issue only where there is a finding, and an XM-001 issue references two elements rather than one.

Three differences drive the adapter between them. Cardinality: one row per element against zero or more issues per element. Absence semantics: a compliant element is a Low row on the first path and nothing at all on the second, so merging naively would make every compliant element appear unassessed by MM-001 and XM-001. Identity: both key on the IFC GUID, so the join key already exists and needs no invention.

The engines sit behind separate feature flags, both defaulting to off. They are deliberately not on one switch. MM-001 runs entirely from disk, while XM-001's loader reads the GC-001 series from the database and must degrade to ‘not assessed’ if that read fails, never to an empty result that would read as ‘no couples found’. Reporting absence of data as absence of risk is the specific failure this separation prevents.

## 13.5  Validation

Both engines are covered by automated test suites — 29 tests for MM-001 and 39 for XM-001. The suites are organised by what each group protects, and three of those groups test the ruleset rather than the arithmetic: that the pack carries an approved status, that its weights sum to one, and that every cell in the compatibility matrix carries a citation. A ruleset that lost a citation would fail the suite before any scoring was exercised.

| Test group | MM-001 | XM-001 | What it protects |
| --- | --- | --- | --- |
| Rule pack contract | 4 | 4 | Approved status, required keys, weights sum to one, every cell cited |
| Scenario verdicts | 7 | 5 | Named cases land in the expected band |
| Data quality / tier semantics | 5 | 3 | Missing input never scored as benign |
| Audit trail | 5 | 2 | Findings carry citations and match their stored score |
| Mechanism-specific | 4 | 21 | Kinetics guard; anode identification, mitigation, separation, floor |
| Output shape | 4 | 4 | Unique issue ids, real element references, silence when compliant |

Table 13.4: Test coverage for MM-001 and XM-001 by group

Two groups carry the arguments made earlier in this chapter. The data-quality group enforces the fail-conservative property: an unclassified environment, an unknown material and an unmapped pairing each raise a data-quality issue, and a separate test asserts that a data-quality issue never presents as a scored verdict. The provisional T5 industrial cell of §13.2 is pinned by its own scenario, so an edit to that value fails the suite rather than passing unnoticed — which is what makes the word ‘provisional’ enforceable rather than decorative.

For XM-001 the single-source contract is itself a test: the pack file is asserted to hold no material potentials, so the galvanic series cannot silently fork into a second copy. The compatibility floor is tested to suppress a compatible pair rather than downgrade it, to vary its threshold by environment, and to fail open on an environment it cannot map — reporting the couple rather than discarding it.

These are unit and contract tests on synthetic fixtures. They establish that the engines behave as their rulesets specify; they do not establish that the rulesets are correctly calibrated against built assets, which is the distinction §14.1 draws between what a test can prove and what only an expert can judge.

## 13.6  Approval record and carried limitations

Both rulesets are approved at version 1.0 with a named approver and a recorded amendment list. Four limitations are carried in the pack rather than hidden.

1.  The T5 industrial severity of 0.85 is provisional. It is the only environment value with no CC-001 counterpart, so it is interpolated rather than borrowed.

2.  Water chemistry — chloride concentration, pH, hardness and dissolved oxygen — is absent from the element schema. Cells assume typical UK potable chemistry, so copper Type 2 pitting in soft-water regions is understated.

3.  Flow velocity is absent, so copper erosion-corrosion above roughly 1.5 m/s and the minimum-flow film maintenance that copper-nickel requires are not modelled.

4.  The digits are a calibration authored for these rulesets, not values quoted from the cited standards. The citations name the standard governing each mechanism; they do not supply the number.

The fourth is the most important and the least comfortable. It is the same distinction §4.6.4 draws between a normative value and a provisional one, applied here to material chemistry: a citation that establishes a mechanism is not a citation that establishes a threshold, and a ruleset that conflates the two would claim more authority than it holds.

# Chapter 14 — The Expert Review Process

## 14.1  Why the process exists

Two of the three components produce output that unit tests cannot validate. A test can prove that an extracted rule is schema-valid and executable; only a domain expert can judge whether it means what the clause means. A test can prove that a composite score matches the published formula; only an expert can judge whether the resulting risk band is engineering-credible for that element.

The generic comparator is deliberately excluded as a review object. It performs deterministic threshold evaluation whose correctness is fully decidable by unit tests, and subjecting it to expert review would spend scarce specialist time on the one component that does not need it. That leaves two review objects: a candidate rule produced from a regulatory clause, and a compliance finding produced by a corrosion engine.

## 14.2  Roles and independence

Five roles carry the process. The Extraction Author is the system itself, producing candidates with confidence, source text and clause reference populated; it may approve nothing. The Reviewing Expert scores candidates against the rubric and records a decision with a rationale. The BIM Coordinator confirms the rule is checkable against the delivered model, holding a veto on IFC-mappability alone. The Accountable Approver publishes approved rules and owns the audit trail, an ISO 19650 information-management responsibility. The Process Owner aggregates rejection reasons and owns the extraction prompt and the engine tables.

Roles are functions rather than people, and one person may hold several on a small project, but two separations are absolute. The Extraction Author and the Reviewing Expert must never be the same individual, and the Accountable Approver must never be the person who authored the amendment being approved. For any rule of mandatory severity the Reviewing Expert must additionally be independent of whoever authored the source specification. This mirrors ordinary design-assurance practice and stops the process degenerating into self-certification.

## 14.3  States and the enforcement gate

Every review object moves through one state machine: DRAFT, IN_REVIEW, AMENDED, REJECTED, APPROVED, PUBLISHED and SUPERSEDED. State is a property of the record rather than of a person's inbox, which is what makes the process auditable after the fact rather than only observable while it runs.

One property of that machine matters more than the rest: only PUBLISHED rules are evaluated. That single constraint is the enforcement gate, and §14.6 records honestly that it is the part of this specification not yet built.

## 14.4  The review rubric

A Reviewing Expert scores each candidate rule on five dimensions from 1 to 5. A rule is approved only if every dimension scores at least 4 and Traceability scores 5. There is no approval with reservations; anything short of that threshold is amended or rejected.

| Dimension | The question the expert answers |
| --- | --- |
| Traceability | Can I find this requirement in the cited clause? |
| Semantic fidelity | Does the rule mean what the clause means? |
| IFC mappability | Can this be checked against a delivered model? |
| Executability | Will the comparator produce a decidable result? |
| Scope correctness | Are the conditions and exceptions right? |

Table 14.1: The five-dimension review rubric for a candidate rule

For a compliance finding the rubric changes to four dimensions at the same threshold: input fidelity, term plausibility, band credibility and action proportionality. The question shifts from whether the rule was extracted faithfully to whether a competent engineer would place this element in this band and act on it this way.

Every rule of mandatory severity is reviewed. For the remainder a stratified random sample of 20% is reviewed, stratified by rule type because the failure modes observed in development cluster by rule type rather than by clause. A further 20% overlap is double-reviewed by two independent experts to measure inter-rater agreement. A Cohen's kappa below 0.6 on any dimension is treated as a defect in the rubric rather than in the reviewers, and triggers a rubric revision before reviewing continues.

## 14.5  Failure classes and the feedback cycle

Expert review is not only a filter. Its primary product is a classified rejection record that drives systematic improvement, so every rejection or amendment is tagged with one failure class and each class routes to a named owner.

| Class | Typical cause | Routed to |
| --- | --- | --- |
| F1 Citation | Clause reference wrong or hallucinated | Extraction prompt |
| F2 Semantic | Operator inverted, threshold or unit wrong | Prompt and few-shot examples |
| F3 Mapping | Target property is not a real IFC property | IFC enrichment maps |
| F4 Scope | Conditions or exceptions dropped | Extraction prompt |
| F5 Granularity | One clause split into too many or too few rules | Section chunking |
| F6 Engine | Corrosion band judged not credible | Engine tables and thresholds |
| F7 Input | Model data read incorrectly | IFC parser |

Table 14.2: Failure classes and the owner each routes to

The cycle runs on the project's weekly coordination rhythm so that review effort and model drop coincide: extraction on Monday, review on Tuesday and Wednesday, triage on Thursday, regression on Friday, publication ahead of the next drop. Any failure class exceeding 10% of a week's decisions becomes a corrective action with a named owner. The Friday step carries the safeguard: a prompt or table change is kept only if the golden-set score does not regress, which is what stops the loop over-fitting to last week's rejections.

Five metrics are tracked per cycle — first-pass acceptance rate, amendment rate, rejection rate by class, median review time per item, and inter-rater agreement on the double-reviewed overlap. A sixth, the defect escape rate of approved rules later found wrong, is the lagging indicator that reveals whether the rubric is calibrated at all.

## 14.6  Implementation status

This specification exists because an earlier draft asserted that expert review validated the engines' risk-band distribution and that a human-in-the-loop safeguard governed LLM-extracted rules, without defining who reviews, against what criteria, at what cadence, or what becomes of the finding afterwards. Defining the process makes the gap between specification and implementation visible, and that gap is stated here rather than left to be discovered.

| Element of the process | Status |
| --- | --- |
| Review flag, confidence score and clause traceability on every rule | Implemented |
| Query for items awaiting review; schema and executability pre-check | Implemented |
| Reviewer-facing interface | Partial — displays rules, but has no scoring form |
| The state machine of §14.3 | Not implemented |
| The enforcement gate — evaluating PUBLISHED rules only | Not implemented |
| Reviewer identity, decision, rationale and timestamp | Not implemented |
| Failure-class tagging and aggregation | Not implemented |
| Review of compliance findings | Not implemented |
| Golden-set regression on prompt change | Blocked — harness calls a missing method |

Table 14.3: Implementation status of the expert review process

One line in that table governs the honesty of the whole claim. Because the enforcement gate does not exist, the comparator evaluates saved rules regardless of whether they have been reviewed, which makes the human-in-the-loop claim partially true rather than true. The minimum viable remedy, in order, is to add a review-state column and gate the comparator's rule query on it, then add a review record capturing reviewer, decision, rationale, failure class and timestamp, then build the scoring form over the existing interface, and finally repair the regression harness. The first two are small schema changes and are the highest-leverage work identified anywhere in this project.

# References

ACI (2019) ACI 318-19 Building Code Requirements for Structural Concrete and Commentary. Farmington Hills, MI: American Concrete Institute.

American Galvanizers Association (2023) Corrosion: Overview of Galvanic Protection. Centennial, CO: American Galvanizers Association.

ASCE (2022) ASCE/SEI 7-22 Minimum Design Loads and Associated Criteria for Buildings and Other Structures. Reston, VA: American Society of Civil Engineers.

ASTM International (2019) ASTM B117-19 Standard Practice for Operating Salt Spray (Fog) Apparatus. West Conshohocken, PA: ASTM International.

ASTM International (2021) ASTM G48-11(2020) Standard Test Methods for Pitting and Crevice Corrosion Resistance of Stainless Steels and Related Alloys by Use of Ferric Chloride Solution. West Conshohocken, PA: ASTM International.

AUCSC (2024) Basic Corrosion Course — Module 3: Galvanic Corrosion. Houston, TX: Association for Materials Protection and Performance (formerly NACE International).

BIMForum (2025) Level of Development (LOD) Specification 2025, Part I. Washington DC: BIMForum. Available at: https://bimforum.org/resource/lod-level-of-development-lod-specification/ [Accessed August 2026].

BS 8539:2012 (2012) Code of Practice for the Selection and Installation of Post-Installed Anchors in Concrete and Masonry. London: BSI Standards.

BS EN 1993-1-4:2006+A1:2015 (2015) Eurocode 3: Design of Steel Structures — Part 1-4: General Rules — Supplementary Rules for Stainless Steels. London: BSI Standards.

buildingSMART International (2021) BCF 2.1 — BIM Collaboration Format Specification. Oslo: buildingSMART International Ltd.

buildingSMART International (2023) IFC 4.3.2 Documentation. Available at: https://ifc43-docs.standards.buildingsmart.org [Accessed April 2026].

CDA — Copper Development Association (2023) Copper Tube Handbook and Technical Notes. McLean, VA: Copper Development Association Inc.

CEN (2003) EN 12952-12:2003 Water-tube Boilers and Auxiliary Installations — Part 12: Requirements for Boiler Feedwater and Boiler Water Quality. Brussels: European Committee for Standardization.

CEN (2011) EN 1998-1:2004+A2:2011 Eurocode 8: Design of Structures for Earthquake Resistance — Part 1: General Rules, Seismic Actions and Rules for Buildings. Brussels: European Committee for Standardization.

CIBSE (2013) TM13: Minimising the Risk of Legionnaires’ Disease. London: Chartered Institution of Building Services Engineers.

CIBSE (2021) Guide G: Public Health and Plumbing Engineering (4th edn). London: Chartered Institution of Building Services Engineers.

CIRIA (2014) C692 — Stainless Steel in Construction: A Review of Research, Applications and Challenges. London: CIRIA.

DIN (2005) DIN 4149:2005-04 Bauten in deutschen Erdbebengebieten — Lastannahmen, Bemessung und Ausführung üblicher Hochbauten. Berlin: Deutsches Institut für Normung e.V. [Withdrawn 2011; superseded by DIN EN 1998-1:2010-12 and DIN EN 1998-1/NA:2011-01].

DIN (2023) DIN EN 1998-1/NA:2023-11 Nationaler Anhang — National festgelegte Parameter — Eurocode 8: Auslegung von Bauwerken gegen Erdbeben — Teil 1: Grundlagen, Erdbebeneinwirkungen und Regeln für Hochbauten. Berlin: Deutsches Institut für Normung e.V.

Eastman, C., Teicholz, P., Sacks, R. and Liston, K. (2011) BIM Handbook: A Guide to Building Information Modelling for Owners, Managers, Designers, Engineers and Contractors (2nd edn). Hoboken, NJ: Wiley.

Evans, U.R. (1960) The Corrosion and Oxidation of Metals. London: Edward Arnold.

FEMA (2004) FEMA P-414 Installing Seismic Restraints for Duct and Pipe. Washington DC: Federal Emergency Management Agency.

Fontana, M.G. and Greene, N.D. (1967) Corrosion Engineering. New York: McGraw-Hill.

HM Government (2022) Building Safety Act 2022. London: HMSO.

HSE (2014) HSG274 Legionnaires’ Disease: Technical Guidance — Part 2: The Control of Legionella Bacteria in Hot and Cold Water Systems (and Part 3: The Control of Legionella Bacteria in Other Risk Systems). Bootle: Health and Safety Executive.

IMOA — International Molybdenum Association (2014) Practical Guidelines for the Fabrication of Duplex Stainless Steels (3rd edn). London: IMOA.

ISO (2007) EN ISO 15329:2007 Corrosion of Metals and Alloys — Electrochemical Testing — Measurement of Electrochemical Impedance. Geneva: International Organization for Standardization / Brussels: CEN.

ISO (2018) ISO 19650-1:2018 Organization and Digitization of Information about Buildings and Civil Engineering Works, Including Building Information Modelling (BIM) — Information Management Using Building Information Modelling — Part 1: Concepts and Principles. Geneva: International Organization for Standardization.

ISO (2018) ISO 19650-2:2018 Organization and Digitization of Information about Buildings and Civil Engineering Works, Including Building Information Modelling (BIM) — Information Management Using Building Information Modelling — Part 2: Delivery Phase of the Assets. Geneva: International Organization for Standardization.

ISO (2024) ISO 16739-1:2024 Industry Foundation Classes (IFC) for Data Sharing in the Construction and Facility Management Industries — Part 1: Data Schema. Geneva: International Organization for Standardization.

Mason Industries (2018) Seismic Restraint Guidelines. Hauppauge, NY: Mason Industries. Available at: https://thehillco.com/wp-content/uploads/2018/03/Seismic-Restraint-Guidelines.pdf [Accessed August 2026].

Mehrbod, S., Staub-French, S., Mahyar, N. and Tory, M. (2019) ‘Beyond the clash: investigating BIM-based building design coordination issue representation and resolution’, Journal of Information Technology in Construction (ITcon), 24, pp. 33–57. Available at: https://www.itcon.org/2019/3 [Accessed August 2026].

NACE International (2016) International Measures of Prevention, Application, and Economics of Corrosion Technology Study (IMPACT). Houston, TX: NACE International.

NASA (2016) NASA-STD-6012 — Corrosion Control and Treatment for Aerospace Vehicles. Washington DC: National Aeronautics and Space Administration.

NFPA (2022) NFPA 13 Standard for the Installation of Sprinkler Systems, 2022 edition. Quincy, MA: National Fire Protection Association.

Prosoco (2019) Prosoco Technical Note 104: Galvanic Action and the Area Ratio Effect in Mechanical Anchors. Lawrence, KS: Prosoco Inc.

Sandvik/Alleima (2023) Corrosion Handbook — Stainless Steels. Sandviken: AB Sandvik Materials Technology.

SMACNA (2024) Seismic Restraint Manual: Guidelines for Mechanical Systems (4th edn). Chantilly, VA: Sheet Metal and Air Conditioning Contractors’ National Association.

WorldStainless / Euro Inox (2025) Stainless Steels in Contact with Other Metallic Materials — Volume 10 (3rd edn). Brussels: Euro Inox.