## Slide 1
Crevice Corrosion
CC-001 Compliance Engine — BIMGUARD AI
Engine: BIMGUARD-CC-001 v1.0.0
Standards: EN ISO 15329:2007 · ASTM G48 Method B · CIRIA C692 · CIBSE Guide G · EN 1993-1-4
Extends BIMGUARD AI beyond galvanic checking — the failure mode invisible to GC-001 alone
Final Master Project | Masters in BIM Management | Zigurat Global Institute of Technology | Group 5

## Slide 2
Why galvanic checking alone is not enough
The corrosion mechanism most likely to be missed — on the material most likely to be specified
Stainless steel is specified precisely because of its galvanic nobility.
That same nobility makes crevice corrosion its dominant failure mode in chloride environments.
GC-001 result (galvanic)
SS316 flanges in a pool plant room:
Galvanic composite score: 0.00
Risk band: LOW
Conclusion: no galvanic risk identified.
CC-001 result (crevice)
Same SS316 flanges, same environment:
Crevice composite score: 0.89
Risk band: CRITICAL
Conclusion: immediate remediation required.
What this means
A galvanic-only tool classifies this installation as safe.
Crevice corrosion will produce through-wall failure within 2–5 years.
CC-001 is not optional — it is necessary.
This finding is the academic justification for the dual-engine architecture of BIMGUARD AI.
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 3
The crevice corrosion mechanism — four stages
Fontana & Greene (1967) — the chemistry that destroys stainless steel in confined spaces
1
Initiation
Confined electrolyte initially identical to bulk solution. Oxygen depletion begins as cathodic reduction consumes O₂ faster than diffusion can replenish it.
2
Differential aeration
O₂-depleted crevice becomes anodic. Metal dissolution begins:
M → M²⁺ + 2e⁻
Electrons travel to oxygenated exterior.
3
Autocatalytic
Metal cation hydrolysis lowers local pH. Chloride ions migrate in to maintain charge neutrality. Passive film destroyed by low pH + high Cl⁻.
4
Propagation
Autocatalytic chemistry is self-sustaining. Corrosion continues even if external conditions improve — until crevice is destroyed or pipe perforated.
Key insight:
Once Stage 3 is reached, the corrosion is self-sustaining — it cannot be stopped by improving the external environment. Prevention must happen at design stage, before the chemistry initiates.
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 4
Critical Crevice Corrosion Temperature (CCT)
The minimum temperature at which crevice attack initiates — ASTM G48 Method B / CIRIA C692
Grade | UNS | CCT (°C) | PREN (typical) | Typical MEP application
SS 304 / 1.4301 | S30400 | −5 | 18–20 | General HVAC, cold water (low chloride environments only)
SS 316 / 1.4401 | S31600 | +10 | 24–26 | Process, pharmaceutical, pool — risk above 10°C in Cl⁻ environments
Duplex 2205 / 1.4462 | S32205 | +25 | 33–38 | Coastal, desalination, aggressive process environments
Super Duplex 2507 / 1.4410 | S32750 | +50 | 40–43 | Offshore, seawater, highly aggressive chloride environments
Titanium Grade 2 | R50400 | +120 | > 40 | Exceptional resistance — used where all SS grades are inadequate
PREN formula (IMOA Design Manual 4th Ed.):
PREN = %Cr + 3.3 × %Mo + 16 × %N
Source: ASTM G48 Method B / CIRIA C692 / Sandvik Corrosion Handbook
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 5
CC-001 scoring model
Three-component weighted composite score — referenced to published standards
Score_CC = (0.35 × geometry risk) + (0.40 × CCT adequacy) + (0.25 × environment severity)
Geometry risk (0.35)
4 classes: Open (0.10) → Moderate (0.45) → Tight (0.75) → Critical (1.00)
14-type joint library maps IFC element type to geometry class.
Tightest geometry = most restricted electrolyte circulation = highest risk.
CCT adequacy (0.40)
Highest weight — most material-specific determinant.
Compares operating temperature against the material's CCT.
Above CCT = risk score 1.00, regardless of geometry or environment.
Environment severity (0.25)
7 classes per EN ISO 15329:2007 wetting classifications.
Chloride concentration determines class.
Pool / coastal / pharmaceutical = highest severity.
Risk bands:
Low < 0.30
Medium 0.30 – 0.55
High 0.55 – 0.80
Critical > 0.80
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 6
14-type joint library — IFC element to geometry class
Maps IfcPipeSegment / IfcPipeFitting classification to crevice geometry risk without requiring joint geometry to be modelled
Code | Joint type | Geometry class | Risk mult. | Code | Joint type | Geometry class | Risk mult.
JT-001 | Butt weld | Open | 0.10 | JT-008 | Victaulic groove | Moderate | 0.45
JT-002 | Socket weld | Moderate | 0.45 | JT-009 | Screwed BSP | Critical | 1.00
JT-003 | Slip-on flange | Moderate | 0.45 | JT-010 | Lap joint flange | Tight | 0.75
JT-004 | Weld neck flange | Tight | 0.75 | JT-011 | Ring-type joint flange | Tight | 0.75
JT-005 | Threaded NPT | Critical | 1.00 | JT-012 | Pipe clamp under insulation | Critical | 1.00
JT-006 | Compression fitting | Tight | 0.75 | JT-013 | Mechanical anchor contact | Tight | 0.75
JT-007 | Push-fit press | Moderate | 0.45 | JT-014 | Unknown / unclassified | Tight (default) | 0.75
JT-014 conservative default: any unclassified IFC joint type is assigned Tight (0.75) — tool always fails safe when joint data is incomplete.
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 7
CC-001 validation results
10 scenarios — all results consistent with engineering expectation
10
validation
scenarios run
4
Critical
findings
3
High
findings
100%
pass rate
vs expectation
Key validation finding:
SS316 flanges in pool plant room · GC-001: 0.00 (Low) · CC-001: 0.89 (Critical)
Demonstrates that stainless steel — the most galvanically noble grade in the series — requires crevice assessment independently of galvanic result.
SS304 flanged pool enclosure
Score: 0.97 Critical — below CCT by 20°C, flanged joint, pool chloride
Duplex 2205 coastal external
Score: 0.42 Medium — CCT adequate (+25°C margin), exposed environment
Titanium process pipe
Score: 0.04 Low — CCT +120°C provides full protection across all environment classes
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 8
CC-001 integration with the BIMGUARD AI framework
Combined risk assessment, dual Pset write-back, separate BCF issues per mechanism
Combined risk assessment function
combined_risk_assessment() runs GC-001 and CC-001 simultaneously.
Combined band = higher of the two individual bands.
SS316 pool plant room: Low (GC) + Critical (CC) → Combined: CRITICAL.
Separate BCF issues per mechanism
GC-001 and CC-001 generate independent BCF issues for the same element.
Different responsible engineer, different mitigation action.
No ambiguity about what needs to be done and who does it.
Pset_CreviceCorrosionRisk IFC write-back
CC-001 writes a property set to the IFC model alongside Pset_CorrosionRisk.
Properties: CreviceRiskScore, CreviceRiskBand, CCTAdequacyScore, GeometryClass, EnvironmentSeverity, RecommendedMitigation, RulesetVersion, AssessmentDate.
Combined asset register
One CSV row per element: GlobalID · GC-001 score · CC-001 score · combined band · cost · programme impact · assigned engineer.
Complete two-mechanism view of every MEP element.
ISO 19650 status: Elements with unresolved CC-001 Critical findings are held at Status S2 (Work in Progress) in the CDE — cannot advance to Shared until the finding is resolved and the model re-checked.
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 9
CC-001 — three conclusions
Crevice corrosion changes the compliance picture
1
Single-mechanism checking is not sufficient. A tool that checks only galvanic compatibility will classify SS316 stainless steel as safe in a pool plant room. BIMGUARD AI — with CC-001 — correctly classifies it as Critical. The two engines are genuinely independent and genuinely necessary.
2
Material nobility is not protection. The most corrosion-resistant stainless grades are more susceptible to crevice corrosion than standard carbon steel in aggressive crevice conditions, because their passive film — the source of their nobility — is exactly what crevice chemistry destroys. CCT is the defining parameter, not PREN.
3
Prevention must happen at design stage. Once autocatalytic crevice chemistry initiates (Stage 3), the corrosion is self-sustaining regardless of external conditions. The CC-001 compliance check, run on the LOD 300 model before fabrication, is the only intervention point at which crevice corrosion can be designed out rather than managed.
BIMGUARD AI | CC-001 Crevice Corrosion Engine | Final Master Project | Zigurat Global Institute of Technology | Group 5