## Slide 1
BIMGUARD AI
Automated BIM Corrosion Compliance Checker
OpenBIM · IFC ISO 16739-1 · BCF 2.1 · ISO 19650
Galvanic Corrosion Engine GC-001 · Crevice Corrosion Engine CC-001
Final Master Project | Masters in BIM Management | Zigurat Global Institute of Technology | Group 5

## Slide 2
The problem BIM cannot currently solve
Corrosion causes predictable, preventable failures — but BIM coordination tools do not check for it
3.4%
of global GDP lost
to corrosion annually
6–10×
cost multiplier: field
vs design-stage fix
0
existing BIM tools check
corrosion risk in IFC
0 pts
Golden Thread evidence
without BIMGUARD AI
Standard BIM clash detection finds geometric conflicts — pipe-on-pipe clashes, services through structure. It does not check whether two correctly-positioned pipes will corrode each other because of their material pairing, joint geometry, or environment. This failure mode is invisible to every current BIM coordination tool.
BIMGUARD AI closes this gap — using data already in the IFC model.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 3
Three research questions
The academic scope that frames this project
RQ1 — Detection from existing IFC data
Can corrosion risk in MEP building services be reliably detected from data already present in standard IFC models, without requiring additional manual input or proprietary BIM authoring tool access?
RQ2 — Dual-mechanism simultaneous checking
Can galvanic corrosion and crevice corrosion be checked simultaneously within one automated workflow, and does the combined assessment detect risks that either mechanism alone would miss?
RQ3 — OpenBIM cross-platform deployment
Can an OpenBIM compliance checking tool — operating exclusively on open standards without proprietary APIs — be deployed effectively across the full range of authoring environments used by different disciplines?
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 4
Why OpenBIM?
A deliberate and academically significant architectural decision
Closed BIM ✗
✗ Revit API only — excludes ArchiCAD, Tekla, Vectorworks users
✗ Proprietary plugins required on every authoring machine
✗ No cross-discipline compatibility
✗ Cannot be adopted on mixed-software projects
✗ Vendor lock-in
OpenBIM ✓
✓ IFC (ISO 16739-1) — any tool, any discipline
✓ BCF 2.1 — issues read by all OpenBIM platforms
✓ No plugins, no proprietary access
✓ Works with Revit, ArchiCAD, Tekla, Vectorworks
✓ ISO standard — internationally applicable
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 5
The BIMGUARD AI five-phase compliance pipeline
IFC file in → five sequential checks → BCF 2.1 issues out
IFC input
1
Spatial filter
C-to-C spacing vs minimum
2
Halo envelope
LOD 350 support reservation
3
Galvanic gate
GC-001 material compatibility
4
Resolution hierarchy
Who moves, how far, cost
5
Executive report
BCF + ISO 19650 + cost avoid
FAIL paths from Phases 1, 2, 3 → all route to Phase 4 for resolution
IFC
Reads IFC 2x3 and IFC4 — any authoring tool (ifcopenshell)
BCF
Outputs BCF 2.1 — every issue has GlobalID, viewpoint, cost, assignee
ISO
ISO 19650 status codes: Work in Progress → Shared → Approved
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 6
Phase 1 — Spatial filter
The check that standard BIM tools miss: metadata-driven insulation clash detection
C-to-C min = (OD₁/2 + T_ins1) + 25 mm + (T_ins2 + OD₂/2) + Thermal displacement
What GC-001 reads from IFC
OuterDiameter from Pset_PipeSegmentOccurrence
Insulation from Pset_CoveringCommon.TotalThickness
System type → default insulation fallback
The Navisworks gap
Navisworks only detects modelled geometry.
If insulation is in a Pset but not modelled as a 3D solid, Navisworks reports PASS.
BIMGUARD reads the metadata — catches what isn't there.
FAIL → Phase 4
If actual C-to-C < minimum:
Hard clash flagged immediately.
Element pair routed to Phase 4 resolution.
BCF issue generated with offset instruction.
Standards: PIP PNE0003 · ASME B16.5 (US) · EN 1092-1 (EU) · ISO 16739-1 IFC schema
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 7
Phase 2 — Halo envelope (LOD 350)
Reserve space now for support steelwork that doesn't exist yet
R_halo = (OD/2 + T_ins) + 100 mm (support buffer) + 150 mm (seismic buffer, if active)
100 mm support buffer
Physical width of Unistrut P1000 + clevis hanger assembly (MSS SP-58 dimensions)
150 mm seismic buffer
Diagonal leg of sway brace per SMACNA / EN 13480-3 — active only when SeismicZone Pset is populated
Halo breach = WARNING
Pipes clear physically but LOD 350 hanger cannot fit — model held at Work in Progress in CDE
The Halo concept is the unique academic contribution of Phase 2.
Most BIM tools are reactive — they check what is in the model. BIMGUARD AI is proactive — it reserves space for what will be in the model at LOD 350.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 8
Phase 3
Galvanic gate — GC-001
Engine: BIMGUARD-GC-001 v1.0.0
Standards: NASA-STD-6012 · WorldStainless / Euro Inox (2025) · IMOA Design Manual 4th Ed. · AUCSC (2024)
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 9
GC-001 — Galvanic corrosion engine
22-material electrochemical series · 7 environment classes · PREN adequacy check
Score_GC = (0.50 × voltage risk) + (0.30 × area ratio risk) + (0.20 × environment multiplier)
Risk band
Score range
BCF priority
Colour
Low
< 0.35
Minor
Green
Medium
0.35 – 0.65
Normal
Amber
High
0.65 – 0.85
Major
Orange
Critical
> 0.85
Critical
Red
PREN adequacy check (stainless steel only)
PREN = %Cr + 3.3 × %Mo + 16 × %N
· E1–E2 (controlled indoor): PREN ≥ 18 → SS304 adequate
· E3–E4 (humid/external): PREN ≥ 25 → SS316 required
· E5–E7 (aggressive/coastal): PREN ≥ 32 → Duplex 2205+
BCF issues generated for Medium, High, and Critical. Low results recorded in asset register only.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 10
Phase 3 (continued)
Crevice gate — CC-001
Engine: BIMGUARD-CC-001 v1.0.0
Standards: EN ISO 15329:2007 · ASTM G48 Method B · CIRIA C692 · CIBSE Guide G · EN 1993-1-4
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 11
CC-001 — Crevice corrosion engine
CCT table · 14-type joint geometry library · 7 environment severity classes
Score_CC = (0.35 × geometry risk) + (0.40 × CCT adequacy) + (0.25 × environment severity)
Grade
CCT (°C)
PREN (typ.)
SS 304
-5
18–20
SS 316
+10
24–26
Duplex 2205
+25
33–38
Super Duplex 2507
+50
40–43
Titanium Gr. 2
+120
>40
Source: ASTM G48 Method B / CIRIA C692
Geometry class
Multiplier
Open (butt weld)
0.10
Moderate (slip-on flange)
0.45
Tight (weld neck flange)
0.75
Critical (threaded / under clamp)
1.00
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 12
The finding that justifies the dual-engine architecture
SS316 flanges in a pool plant room
GC-001 galvanic score
0.00
LOW — SS316 is among the most noble
metals in the galvanic series. No risk.
CC-001 crevice score
0.89
CRITICAL — SS316 CCT = +10°C.
Pool plant room regularly exceeds this.
Flanged joint geometry = Critical.
A galvanic-only tool classifies this installation as safe. BIMGUARD AI classifies it correctly — as a Critical crevice risk that will fail within two to five years.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 13
Why both engines are necessary
The combined_risk_assessment() function runs GC-001 and CC-001 simultaneously
Combined risk band rule
The combined risk band = the higher of the two individual bands.
SS316 pool plant room: Low (GC) + Critical (CC) → Combined: CRITICAL
Separate BCF issues per mechanism
GC-001 and CC-001 generate separate BCF issues for the same element — because the responsible engineer and the mitigation action differ.
Pset write-back to IFC model
Both Pset_CorrosionRisk and Pset_CreviceCorrosionRisk are written to the IFC model — creating a permanent, machine-readable compliance record.
Asset register CSV export
Combined asset register: GlobalID · service type · GC score · CC score · combined band · cost · programme impact — one row per element.
Both engines also run the PREN adequacy check — ensuring the specified stainless grade is adequate for the environment class, regardless of the corrosion mechanism under assessment.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 14
Phase 4 — Resolution hierarchy
Which pipe moves, how far, at what cost and schedule impact — decided automatically
T1
Gravity priority
Slope attribute > 0 → pipe is immovable.
No algorithm can override a fixed drainage gradient.
Both sloped → Systemic Design Failure → human review required.
T2
Cost delta
Calculate reroute cost for each pipe:
Material rate × length + labour complexity multiplier × length + fittings.
If delta > 20% → cheaper pipe moves automatically.
T3
Schedule risk
If cost delta < 20% → evaluate programme impact.
Orbital weld: +3 days per weld. Flanged restricted access: +1 day per joint.
Lowest programme impact wins. Equal → smaller bore moves.
BCF output: Element GlobalID · offset direction & magnitude (mm) · estimated cost (£) · working days impact · discipline engineer assigned
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 15
Phase 5 — Executive report and ISO 19650 output
Three audience-specific deliverables from one compliance run
Discipline engineer
BCF 2.1 issue file — GlobalID, viewpoint, resolution instruction, cost, assignee
BIM manager
Compliance dashboard — pass/fail by phase, open vs resolved issues, CDE container status
Client / project manager
Cost avoidance summary — design-stage cost vs equivalent field-stage cost at 6× multiplier
ISO 19650 status mapping:
S2 — Work in Progress
Unresolved Phase 1/2 failures
S4 — Shared (NCR)
Phase 3 warnings present
Status A — Approved
All phases pass
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 16
The BIMGUARD AI Streamlit application
Python · Streamlit · ifcopenshell · Plotly · BCF 2.1 — runs at localhost:8501
1
Data ingestion
IFC upload or 25-element demo.
Point cloud upload or synthetic.
Single-button compliance run.
2
Model overview
MEP element table — filterable.
Material inventory chart.
Element count by service type.
3
Corrosion compliance
Risk distribution pie chart.
3D spatial risk map (Plotly).
Full results table + CSV export.
4
Point cloud compare
IFC centroids overlaid on
point cloud in 3D space.
Deviation analysis.
5
BCF issue manager
Issues by risk band.
Engineer assignment chart.
BCF 2.1 ZIP download.
6
Schedule & cost
Gantt: baseline vs delayed.
Cost by band and mechanism.
Issue-level breakdown.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 17
Validation results — 25-element synthetic MEP dataset
Designed to represent an unreviewed commercial plant room specification
9
Critical risk
findings
7
High risk
findings
9
Medium risk
findings
25
BCF issues
generated
Key finding:
SS316 flanges in pool plant room — GC-001 score 0.00 (Low) · CC-001 score 0.89 (Critical). A galvanic-only tool classifies this as compliant. BIMGUARD AI correctly flags it as a Critical crevice risk requiring immediate attention.
Validation demonstrates that GC-001 and CC-001 detect distinct and non-overlapping failure modes. Neither engine alone is sufficient for a comprehensive corrosion compliance assessment.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 18
Blue Halo results — hospital MEP case study
Hospital plant corridor, 3.5 m soffit height · γa = 1.5 · seismic demand 0.35 · one run per brace family
380 mm
Angle iron Halo
2 conflicts
200 mm
Threaded rod Halo
1 conflict
120 mm
Cable Halo
0 conflicts
12.2 m
Transverse spacing
NFPA 13 Ch. 18
Recommendation:
Cable bracing — the only family that resolves the node set without a design change. Smallest footprint, clear of both the sprinkler main and the conduit.
Reserved at LOD 300, the conflict reaches the designer while ductwork and conduit can still be moved. Mehrbod et al. (2019) record a comparable reroute costing six weeks once services were installed.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 19
The number that matters to a client
£170,600
Total estimated
remediation cost
(design stage)
162
Working days
programme delay
avoided
Cost avoidance at 6× field multiplier:
Design-stage cost £170,600 × 6 = £1,023,600 field cost → £852,000 avoided
For Semiconductor Fab projects where a single day of production downtime can exceed the entire reroute cost, the multiplier is conservative — often 20× or higher.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 20
Three academic contributions
What BIMGUARD AI adds to the body of knowledge
1 — Corrosion compliance from IFC metadata without geometric modelling
Demonstrates that engineering-level corrosion risk assessment can be performed on property set metadata without requiring insulation, supports, or joint geometry to be modelled as 3D solids. Addresses a fundamental limitation of all current BIM clash detection tools.
2 — White Box Architecture for AI-assisted compliance checking
Establishes a methodology in which every compliance decision is traceable to a named standard and a specific threshold. Demonstrates that transparent, auditable rule-based compliance checking is viable in a BIM context — and preferable to black-box ML approaches for regulatory acceptance.
3 — Halo Envelope: proactive LOD 350 space reservation at LOD 300
Introduces a formal method for reserving space for LOD 350 support steelwork within a LOD 300 coordination model. Addresses a recognised and costly gap in current BIM coordination practice — the 'Coordination Fatigue' problem where 80% of meeting time is spent deciding who moves.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 21
Further development roadmap
Three planned modules and two integration streams
MC-001
MIC module (Microbially Influenced Corrosion)
Dead-leg pipework · stagnant water · under-insulation scenarios. Relevant to healthcare, pharmaceutical, food processing, Legionella risk management.
FC-001
Fire compartmentation module
Penetration sealing compliance · smoke control zoning · compartment integrity checking from IFC spatial data. Second major compliance domain alongside corrosion.
BMS
BMS integration
Dynamic risk score updating from live Building Management System data. Transforms BIMGUARD from design-stage tool to continuous operational risk monitor.
IDS
IDS validation layer
Information Delivery Specification validation — checking that the IFC model contains the required Psets before running compliance engines. Prevents false Low results from missing data.
AI
LLM natural language interface
Conversational query interface against the NotebookLM knowledge base — enabling engineers to ask 'why is this element flagged?' and receive a standard-referenced explanation.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 22
Regulatory context — the Golden Thread
BIMGUARD AI as a compliance instrument, not just a coordination tool
Building Safety Act 2022 — Golden Thread requirement
What the Act requires
For higher-risk buildings: information about the building must be created, maintained, and passed through each lifecycle stage in a form that is accurate, up to date, and accessible to those who need it.
What BIMGUARD AI provides
Machine-readable compliance records embedded in the IFC model (Pset_CorrosionRisk, Pset_CreviceCorrosionRisk) and in BCF issues with full audit trails — standard-referenced, version-controlled, timestamped.
ISO 19650 adoption in 70+ countries means BIMGUARD AI's status code output — S2, S4, Status A — is internationally applicable. The tool is not UK-specific: the corrosion standards are international, the IFC format is global, and the BCF output works in every OpenBIM platform.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 23
Conclusions
Three research questions answered
RQ1
Corrosion risk can be reliably detected from standard IFC data. The material, spatial, and zone metadata required by GC-001 and CC-001 is within the scope of standard LOD 300 models and is routinely populated in well-authored IFC exports.
RQ2
The dual-engine approach detects a significant class of risks that single-mechanism checking misses. The pool plant room finding — 0.00 galvanic, 0.89 crevice — is the definitive validation of this claim.
RQ3
The OpenBIM architecture, using IFC as the sole input and BCF 2.1 as the sole output, has been validated as a viable cross-platform compliance checking approach. No proprietary access was required at any stage.
BIMGUARD AI | Final Master Project | Zigurat Global Institute of Technology | Group 5

## Slide 24
BIMGUARD AI
Automated BIM Corrosion Compliance Checker
OpenBIM · IFC ISO 16739-1 · BCF 2.1 · ISO 19650
GC-001 Galvanic Engine · CC-001 Crevice Engine · Python · Streamlit · ifcopenshell
Questions?
Masters in BIM Management · Final Master Project · Group 5
Zigurat Global Institute of Technology